## HTR - Open Issues
EPNR Working Group - HTR Workstream Workbook (07 August 2025)
Issue ID |  | Description of Issue | Priority | Simple or Substantive | Governance or Technical | Lead | Support | Status Update (11 July) | Status Update (28 August) | Status Update (2 October 2024) | Status Update (10 October 2024) | Consultation Proposals (29 November 2024) | Status Update (10 July 2025) | Status Update (7 August 2025)
Issue 3 | I3 | Definition of contingency events versus credible contingency events and how this may flow on to pre-contingent events. The definition of credible contingency events currently doesn’t align with the AEMC definition which relates credible to things like weather conditions and present threats. | High | Substantive | Technical | Noel (Rio) | David (HP); Lekshmi (BP), James (ISO); Njabulo and Bec (BHP) | This issue is being addressed by the review into Subchapters 7.3 and 7.4 of the PNR currently being conducted by the ISO. Interested parties can contribute to that review early by approaching the ISO directly, or by approaching Noel and group to consolidate inputs to the ISO. | Paper submitted to ISOCO on the 7.3/7.4 review. These issues will be dealt with in that review. |  | ISOCo draft paper is out, group will review to see whether it addresses this issue. If not, recommendation to come to next meeting. | Align the PNR and HTR to have a common definition of credible and non-credible contingency events, adopting the definition in line with AEMC. | Group to provide drafting instructions, reflecting on AEMC public consultation responses as part of development. | No update. Rio to prompt Noel to confirm status.
| I36 | Requirements for generation to ride through multiple consecutive power system disturbances including minimum number of disturbances rode through within a specific period. | Moderate | Substantive | Technical |  |  | No considerable progress given it is substantive and technical. Consideration given to gather historical fault data to help determine the limits
Issue 4 | I4 | Consider requirements to update voltage and frequency standards in accordance with proposed legislative changes to voltage and frequency requirements. | High | Simple | Technical | David (HP) | Nik (APA); Njabulo and Bec (BHP); Noel (Rio), James (ISO) | Recommended option: adopt standards in WEM regulations - outstanding issues: what is a low voltage connection (refer to papers for Item 5 at p16) | Ready for drafting. |  | Closed. | Update the HTR to reflect the new voltage setting to a nominal voltage of 230V with upper limit of 254V and lower limit of 207V. There may be some non-distribution network areas where this may not apply. | Proceed to drafting. | See Status Update (10 July 2025)
Issue 5 | I5 | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including review of the target frequency recovery times under Section 2.2.1 (25 minutes at 48 Hz) may have adverse impacts on system security. | High | Substantive | Technical | David (HP) | Nik (APA); Shervin and Scott (Woodside); Lekshmi (BP); James (ISO); Njabulo and Bec (BHP); Noel (Rio) | Work has commenced on scoping the required modelling. The current expectation is that a first draft of the scoping of issues, and the work required for each issue, is to be presented at next meeting of the EPNRWG HTR Workstream. | All these issues are about setting a value in the HTR relating to performance of the system. This requires supporting technical analysis (est 2-3 months). A SoW for power system studies was included in the meeting pack. WG to review SoW and provide feedback, then lead will incorporate comments and circulate a new version to finalise at the next meeting. |  | An updated and more detailed SoW is to be circulated to the group soon. There are no fundamental changes to the previous SoW. | Investigations and power system studies to be done with the following scope: • review critical fault clearing times; • review generator ride through requirements; • review system islanding scheme and settings; • rate of response; and • review of frequency operating standards. • Allocating responsibility and identifying funding will be necessary to deliver this modelling scope. | Draft scope developed. ISO willing to lead, but would need funding to complete studies. | See Status Update (10 July 2025)
| I6 | Frequency variations - do we need to lower the single contingency event limit due to increasing penetration of renewables / less system inertia e.g. NT has 47 Hz. | High | Substantive | Technical
| I15 | Currently requirement is for up to 4 Hz per second. This requirement has been updated in the WEM Rules. | High | Substantive | Technical
| I16 | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: - Review Section 3.3.3.3(f) - Absorption of reactive power is helpful under some circumstances and may be required for longer periods. Review clause in context of new operating environment. - Most OEMs struggle to achieve the requirement for any pre-fault absorption of reactive power to be terminated within 200 ms after clearing of the fault. Further, from a system perspective, it would not be optimal if all generators stop absorbing after 200 ms. - The WEM Rules have changed this clause (as did the proposed updated to the WP TR). | High | Substantive | Technical
| I17 | Consider continuous uninterrupted operation requirements in section 3.3.3.3(h). It may not be prudent for the system if all generators follow this requirement simultaneously. Whilst a small system like NWIS might benefit from it, this needs to be confirmed with further studies. Also need to define the fault clearance time to comply to this requirement. This clause has been changed in the WEM Rules. Further, we note that some wind generators have not been able to meet this requirement. | High | Substantive | Technical
| I19 | The identified rate of response is difficult for some OEMs of non-dispatchable generating units to achieve – the current requirement is achieving 90% within 2 seconds and new output to be sustained for no more than 10 seconds. The minimum requirement of WEM rules (12.6) states asynchronous machines to meet 60% of the freq response in 6 seconds and 90% by 15 seconds. Related clauses in the WEM Rules to consider are: – A12.6.3.2 which provides more achievable requirements than the current Pilbara HTR. – A provision for negotiating the standard is requested. | High | Substantive | Technical
| I34 | ROCOF and include df/dt for under frequency load shedding and/or under frequency islanding. Determine if df/dt is used for islanding only, or if it can apply to ufls too. | Moderate | Substantive | Technical
| I14 | Renewable generation could comply, but the requirement of 460 ms ride through is overly onerous. We suggest this is revisited system wide to test suitability given it is inconsistent with other countries. The interpretation of the wording should be clarified as it is not clear if this a requirement or optional (Western Power historically tested compliance with this an equivalent clause with some flexibility in the interpretation). | High | Substantive | Technical |  |  | Work started. Support team meeting in two weeks. Proposal to be shared around the end of July. | Recommendation has been made. WG to provide feedback on paper (circulated in meeting papers). Note, recommended option will need to be checked via system study before implementation. |  | Closed. Proposal can be included in consultation paper. | Conduct a pre-requisite engineering and power system analysis on fault clearance times and choose the preferred option of the analysis outcome. Options are to retain status quo, or to redefine UVRT magnitude, duration, and envelope shape. | Propose to merge with Issue 5
Issue 7 | I7 | Consider requirements for NSPs to specify NWIS power system strength requirements and complete necessary assessments as renewable penetrations increases to ensure power system security. | High | Substantive | Goverance & Technical | Nik (APA) | Najbulo and Bec (BHP); James (ISO); Noel (Rio); Lekshmi (BP) | Discussions have started but output not yet available. | Recommendation document to be circulated for next meeting. EPWA to circulate latest WEM work on this topic when it is available. | WEM material included in meeting pack. Discusses the basis for making PSSR standards, not the standards themselves. | EPWA has circulated latest WEM work including this topic. WG will use the material to organize recommendations aimed to be reported on the next meeting | Develop a framework for the management of system strength within the NWIS, leveraging the work undertaken by the SWIS PSSR Standards Working Group. | Group to adopt and adapt SWIS material into model for Pilbara. To provide a high level assessment of level of effort in each area at the August meeting. | Update to be provided for September meeting. Feedback will be sought from wider group.
Issue 8 | I8 | Consider wholistic review of the treatment of Battery Energy Storage Systems and inverter based generating units, including clarity on which sections of the rules apply for these generating units. | High | Substantive | Technical | Peter (ISO) | David (HP); Noel (Rio); Nik (APA); Njabulo and Bec (BHP) | The ISO is looking at resourcing to progress work; and may look to engage an external consultant. In the interim, support group will convene meeting to progress work to the extent practicable and, as appropriate, leverage analogous measures developed as part of the PSSR review. | Proposal to come to next meeting. |  | WG is still working on recommendation for storage and other inverter techs in the PNR and HTR. | In the medium term, amend HTR Clause 3.3 to address specific areas where the applicable technical standard not defined for dispatchable, non-synchronous generation. • HTR 3.7(b) allows NSP and ISO to define technical performance standards for BESS, with respect to injects, by leveraging clause 3.3; and • fixing gaps in clause 3.3 will allow 3.7 to continue to operate appropriately. In the long term, rewrite section 3.7 to include comprehensive requirements for inverter-based storage facilities. Provide definitions in the HTR for “grid forming”, “grid-following” and for the unique characteristics of grid-forming technology such as “synthetic inertia”. | Group to identify specific changes required to clause 3.3 defining user standards for generating facilities to close gaps, such that it can continue to be adapted (per cl. 3.7) for storage works in the short to medium term. Group to continue to work on fit for purpose comprehensive inverter performance standards, to be adopted in the longer term, drawing on SWIS work and others. | To be presented at October meeting.
| I9 | Reference to grid forming and grid following inverter technology may be helpful, with specific regard to the differences in the technical performance between the differing technologies. A definition here may be helpful as there doesn’t appear to be a clear definition on what is grid forming, grid following, or what has virtual synchronous generator performance. | High | Substantive | Technical | [5 empty] | Still needs more input from WG members and experts.
| I12 | Requirements for storage devices to provide network support services (frequency and voltage support) when operating in load/charging mode to enhance power system security/flexibility. Currently the HTR requires storage devices to act as consumer equipment when withdrawing power from the network. | High | Substantive | Technical
Issue 10 | I10 | Additional requirements for dynamic performance on asynchronous inverter connected generation e.g. damping capability for reactive power and active power control systems for inverter connected generation. | High | Substantive | Technical | Njabulo (BHP) | Nik (APA); David, ISO | Recommendation - new HTR for generator requirements and obligations (refer to meeting papers for Item 5, at pp17-21). Updated paper with preferred option to be provided to the EPNRWG (HTR). | Recommendation paper circulated. WG to provide feedback on paper (circulated in meeting papers). |  | Closed. Proposal can be included in consultation paper. | Realign the rules to the increasing penetration of inverter-based generation in NWIS. | Group will provide drafting instruction for August meeting. | Proceed to drafting. Clause 2.2.8.
Issue 11 | I11 | Additional requirements for inverter connected generation response to power system disturbances, such as required magnitude of reactive current injection/absorption to support the power system during and post power system disturbances. | High | Substantive | Technical | Njabulo (BHP) | Nik (APA); David, ISO |  |  |  |  | Review HTR clause 3.3.3.3(g) and consider including quantifiable measures of reactive current injection/absorption during fault or post fault. | Group will provide drafting instruction for August meeting. | Proceed to drafting. Clause 3.3.3.3(g)
Issue 13 | I13 | Definition and use of 'energisation' vs 'commercial operations' is inconsistent throughout the HTR and PNR. Clarity is required about the process and what actions are required from each party at which stage. Inclusion of data to be submitted with connection applications (See Horizon Power Tech Rules Sections 3.3.2, 3.4.3, 3.6.5, and Attachments 3-10). | High | Substantive | Governance & Technical | Peter (ISO) | David (HP); Njabulo and Bec (BHP), Nik (APA) | Work in progress - Proposed solution/recommendation to EPNRWG to be provided in advance of next WS2 meeting. | Proposal to come to next meeting. |  | Draft paper is being prepared and will soon be distributed and discussed with the support group | Add a new definition to PNR and HTR for “commercial operation”. Move the HTR definition of “energisation” to the PNR, amend definition in the HTR to point to PNR definition. Substitute the current PNR references to “energisation” with “commercial operation”. Add a new PNR rule dealing with process to obtain authorisation for energisation for the purposes of testing and commissioning. | Group will provide drafting instruction for September meeting.
| I37 | Inclusion of Testing requirements and test details for connection of Generating Units (See Horizon Power Tech Rules Attachment 11). Dispatchable and non-dispatchable generator testing and compliance requirements and R2 model validation. What are the non-dispatchable unit testing requirements, and how does this differ to dispatchable units. | Moderate | Substantive | Technical | [5 empty] | The WG is likely to recommend a minimum standard and format to accomodate the different information requirements of different NSPs. | Generator testing requirements should be included in an HTR attachment. The requirements should cover minimum standards as well as special tests required by the NSP. The requirements do not need to cover microgrids. Tests for battery storage, IBR and non-dispatchable generation should draw on rules from other jurisdictions. | Group to leverage existing standards to provide instructions for definitions, using Horizon testing schedule as starting point for an HTR attachment. Group to provide completed table for September meeting.
Issue 18 | I18 | This is currently 0.05 Hz. The point at which the dead band is measured is unclear in the current drafting and needs to be updated. The WEM Rules have been revised to be +/-0.025 Hz around 50.0 Hz (refer to A12.6.1.9). | High | Simple | Technical | Lekshmi (BP) | Njabulo and Bec (BHP), ISO | Work started. Support team meeting in two weeks. Proposal to be shared around the end of July. | Recommendation has been made. WG to provide feedback on paper (circulated in meeting papers), otherwise ready for drafting. |  | Closed. Proposal can be included in consultation paper. | Redefine the dead band of a generating unit to be less than or equal to ±0.025 Hz around 50 Hz, unless an adjustable dead band is agreed to in the access contract. | Proceed to drafting. | See Status Update (10 July 2025)
Issue 22 | I22 | Consider requirements regarding disturbance monitoring and synchrophasors. | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP); Noel (Rio); Nik (APA), ISO | - | Proposal to come to next meeting. |  | Not much progress. WG is looking into better monitoring, but nothing specific yet to recommend. | • Update HTR Section3.3.4.1 (d)(3)(a) to include synchrophasor as an acceptable measured value as determined by the relevant NSP. • Make remote monitoring compulsory • Develop a procedure to define data formats, data exchange protocols, and allow ISO access to synchrophasor data • Check proposed wording for WEM/SWIS to ensure alignment where possible. | Proceed to drafting to include a head of power for ISO to define a data format procedure. In parallel, the working group can continue to meet to discuss data exchange formats (etc.) and support to drafting. Mandatory high speed data recordersfor new faciliies are part of the proposal, with the NSP able to capture data from a disturbance in the system to see how volatge and frequency is reacting in different sections in the system. The ISO emphasised the importance of it being able to access this type of information to perform its function to investigate poser system disturbances. | See Status Update (10 July 2025)
Issue 23 | I23 | Consider update to Figure 3.3 noting the four-quadrant capability of inverters. | Moderate | Simple | Technical | David (HP) | Nik (APA); Njabulo and Bec (BHP), ISO | - | Proposal to come to next meeting. |  | The paper that has recommended updates on the HTR has been submitted | Update the clause 3.3.3.1(c)(4) and Figure 3.3 of the HTR to cater for battery energy storage units. This should align with the outcomes of holistic review of treatment of BESS and inverter-based generation. | Proceed to drafting. | See Status Update (10 July 2025)
Issue 24 | I24 | Clarify treatment of ambient temperatures in the context of Section 3.3.3.1. Clarify distinction of using ‘nameplate’ vs ‘derated capacity’ when determining which set of generator compliance rules should apply. | Moderate | Simple | Technical | David (HP) | Lekshmi (BP); Njabulo and Bec (BHP); Noel (Rio), Nik (APA), James (ISO) | - | Proposal to come to next meeting. |  | Urgently working on this issues. Draft paper expected to be circulated before next meeting. | Clause 3.3.3.1 (reactive power) must be updated to provide clarity on ambient temperature, using a method similar to WEM where NSPs will determine the ambient temperature based on 1% probability of exceedance. | Proceed to drafting, although further research into ESM Rules will be required to support drafting. Further, the ISO will check the proposal to see if recent experience could assist or impact recommendation. | See Status Update (10 July 2025)
| I25 | The temperature dependency is a critical factor in the Pilbara that is not adequately considered in the Pilbara HTR. The higher temperatures in the Pilbara will affect the generator’s ability to comply with maximum output requirements (or the maximum output that can be expected). Reactive power related requirements are linked to temperature, whereas historical versions of the rules including the current Pilbara HTR have not linked active power to temperature. This issue should be resolved in the Pilbara HTR to allow the network operator to have a more realistic understanding of what the generation is able to and expected to achieve. In the WEM, wind farms struggle to meet the reactive power capability requirements at 40 degrees (for example A12.2.3.2). However, WEM Rules are more realistic where consideration of temperature is concerned. Of note: – Reactive power capability in clause 3.3.3.1 on possible map with locations and ambient temperature. – Active power capability might need to be de-rated for the wind and solar farms above certain temperatures. This may be a gap in the existing Pilbara HTR as we were unable to identify the relevant clause. – Recommend a review of clauses that refer to “ambient temperature” in addition to the above to ensure suitability. | Moderate | Simple | Technical |  |  | - | Proposal to come to next meeting.
Issue 26 | I26 | Inclusion of Monitoring and Control Requirements (See Horizon Power Tech Rules Section 3.3.4). | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP), Nik (APA) | - | Proposal to come to next meeting. |  | Paper almost ready to be circulated. | • Update clause 3.5 to require mandatory monitoring and control capability of distributed energy resources. • Undertake a general review of clauses 3.3.4 and 3.4.9 of the HTR to consider RME/RCE requirements. | Group to review status, and identify specific changes. | Drafting instructions to be provided for September meeting.
Issue 27 | I27 | Consider requirements for pole slip protection, e.g. where Critical Fault Clearance time issues exist. | Moderate | Simple | Technical | Nik (APA) | David (HP); James (ISO); Njabulo and Bec (BHP); Noel (Rio) | Support group met 06/06/24 and agreed to develop a proposed a set of minimum requirements for generating unit protection, aligned with rating, location and technology. | Recommendation circulated. WG to provide feedback on paper (circulated in meeting papers). |  | Closed. Proposal can be included in consultation paper. | Update the HTR to provide the minimum and recommended protection elements for majority of generating units. | Nik to review paper and confirm whether to proceed to drafting. | Drafting instructions to be provided for September meeting.
Issue 28 | I28 | Review of fault level management on the system: - Consider minimum fault rating requirements for Transmission plant at significant network nodes, and fault level management. - Consider potential requirements for limitations on maximum fault levels on the system and consider providing guidance on the calculation of fault levels. Define credible versus ultimate case. | High | Substantive | Technical | David (HP) | Noel (Rio); James (ISO); Njabulo and Bec (BHP), Nik (APA) | Research into comparative systems with multiple NSPs required (e.g. NEM and US markets). Support group to assist issue lead with research. | Group is developing a short SoW for a quick review of how other markets allocate responsibility for managing fault levels, and protocols for managing interconnected networks. RBP to perform review once scope specified. | Review paper included in meeting pack. | Draft paper is almost ready - working on comments and incorporating the last element of Fault Level Management. There are recommendations on setting Maximum and Minimum Fault Level Requirements as per the international scan. | • Develop table of minimum fault withstand ratings for new plant (based on review of available plant, and possibly Horizon Power Technical Rules Tables A13.1, A13.2, A13.3) and include in the HTR. • Establish a procedure or update an existing procedure to introduce the requirement for NSPs to assess fault levels as part of new connections and system changes. • Include in the HTR a note which requires maximum fault levels at any point will not exceed the minimum fault withstand ratings | Group to work on specifics for first bullet. Proceed to drafting for remainder. | Drafting instructions to be provided for September meeting.
Issue 29 | I29 | Consider requirements adequacy of black start requirements/arrangements. | High | Substantive (study likely) | Technical | Peter (ISO) | David (HP); Njabulo and Bec (BHP) | Under the Rules the ISO may create a blackstart protocol, however there is not one in place yet. There is potential for this to be considered as part of the ISO's review of Subchapters 7.3 and 7.4. If it is not, this Issue can be revisited. | ` |  | This issue is not about the definition or procurement of black start service, rather about having provisions to relax HTR standards for all connected parties in recovering from system black. ISO to consider. | Add a drafter’s note to the PNR giving system restart as an example where it may be impractical to maintain the system inside the Technical Envelope, with the following considerations: • System restart plans in the Pilbara rely on fracturing the power system at points of interconnection • Adequate synchronisation points between registered networks are essential • Explore a requirement in the PNR or HTR mandating at least one network synchronisation point | Proceed to drafting on DN. Working group to develop drafting instructions to mandate a requirement for at least one network synchronisation points between networks, allowing for an ordered restoration of the power system. | Drafting instructions to be provided for September meeting.
Issue 30 | I30 | Connection Point Compliance parameters and definition (including negotiated vs ideal rules - with particular consideration for brownfield plant vs greenfield). Consider if any updates required to facilitate or improved the treatment of Connection Point Compliance measures. | High | Substantive | Governance & Technical | Shervin and Scott (Woodside) | David (HP); Noel (Rio); Njabulo and Bec (BHP), Nik (APA), James (ISO) | Discussed 'circular legal argument' - that compliance with HTR, would invalidate status as a CPC Facility construct in PNR. Working group discussed and agreed to review (the relevant sections of the) Access and Connection Procedure and identify any deficiencies (if there are any). Consensus that there needs to certaint around status of CPC measures (i.e. being temporary or enduring) and appropriate change management mechanisms (i.e. any wholesale changes or departures need to be notified). | Under the current PNR, CPC can't progress unless there is a non-compliance with HTR. This is a process issue not a technical one. There is no point developing CPC measures in the HTR until this is addressed in PNR. Lead to provide 1 page writeup of the issue, so it can be added to the PNR issues list and incorporated into the work of the PNR Workstream. | Issue discussed by Issue Lead and Support. Meeting miuntes provided for further discussion at next meeting. | Closed. Issue transferred to PNR workstream consideration of HTR derogation approach. | Amend PNR requirement which requires non-compliance in order to qualify for CPC status. (also see section 6.3). | Proceed to drafting to fix circular issue. Leave remainder until process is complete for at least a couple of CPC facilities. | See Status Update (10 July 2025)
Issue 32 | I32 | Update Critical Fault Clearing Times at Dampier and Cape Lambert 33kV to reflect recent system changes and approved derogations. | Moderate | Substantive (study likely) | Technical | Peter (ISO) | Noel (Rio); David (HP); Njabulo and Bec (BHP), Nik (APA) | - | There are two parts to this action. 1. What should CFCTs be set at in the long term. This is included in the I5 study scope. 2. Interim changes to CFCT values based on existing derogations. Lead to document interim proposal to update HTR to match existing derogations. |  | Recommendations still to be documented. | Amend HTR Table 2.10 to modernise and simply MFCTs • Remove row for 33 kv HP-Rio tie lines • All 33 kv systems will be subject to MFCT of 300ms • If ‘slower’ clearing times can be justified by the host NSP, based on CFCT studies, the HTR should allow this to be accommodated. • If faster clearing times are needed for interconnectors, this can be implemented under HTR clause 2.6.5 “critical fault clearing lines” | Proceed to drafting. | See Status Update (10 July 2025)
| I33 | Overall review of visit of maximum fault clearance times to ensure alignment. Currently there is misalignment between Western Power, Horizon Power and Rio Tinto technical rules. | Moderate | Substantive (study likely) | Technical |  |  | -
Issue 35 | I35 | Requirements on NSPs to enact special protection schemes to manage network congestion/instability as required to enhance system security. However, this shouldn’t be the sole option to manage security issues – network augmentation and re-dispatch are other methods by which this can be achieved. Generators and loads to possess compliant control systems to facilitate operation of required network special protection schemes to be specified in connection agreements. | Moderate | Substantive | Technical | Njabulo (BHP) | Nik (APA), ISO | EOIs to help issue lead progress issue requested. | Proposal to come to next meeting. Still seeking additional support group members. | Recommend HTR includes defined standards for managing certain non-credible contingencies (criteria defined in HTR), similar to those used in NEM. | Recommendation paper almost ready, to be circulated to WG. | Introduce requirements into HTR around select non-credible events (similar to ‘protected events’ in the NEM). High consequence non-credible events should be brought in line with other NSP practices in Australia. | Group to provide drafting instructions for September meeting.
Issue 38 | I38 | Requirements for NSP to verify integrity of the UFLS scheme across the NWIS network via periodic tests and publish an annual performance report based test results and actual power system UFLS events, this will provide confidence to all customers of UFLS performance integrity and power system security. | Moderate | Substantive | Technical | Njabulo (BHP) | Ben (Woodside), ISO | Issue clarification provided. Broad agreement that proactive measures to ensure integrity of UFLS required, though these measures need to be fit-for-purpose - more likely to be routine consideration and notification of UFLS figures to ISO (rather than annual testing requirement). Next steps draft wording for consideration. | Recommendation has been made. WG to provide feedback on paper (ciculated as part of meeting papers). Ready for drafting. |  | Recommendation paper almost ready, to be circulated to WG. | Require periodic tests, annual publication of test results, and reporting on performance following contingency events. | Group to provide drafting instructions for September meeting. | Proceed to drafting, based on similar functions for system restart. Option to give ISO function to consult with NSPs on a testing regime, review results, and publish its findings. ISO also has function to review contingency events, and this includes any UFLS triggered.
Issue 40 | I40 | Overall review of referenced standards, noting that some standards have more recent versions than those referenced. | Low | Simple | Technical | David (HP) | Njabulo and Bec (BHP) | - | Proposal to come to next meeting. |  | Recommendation paper expected to be submitted by the next meeting. | HTR explicitly states that the most recent version of all standards should be referenced to ensure compliance and accuracy. Remove any specific references to the applicable year, such that the most recent version always applies. | Proceed to drafting. | See Status Update (10 July 2025)
Issue 41 | I41 | Better clarity required for definitions of distribution feeder / interconnector / tie (undefined but included in HTR Table 2.10). | Low | Simple | Technical | Peter (ISO) | Noel (Rio); Njabulo and Bec (BHP), Nik (APA) | - | Proposal to come to next meeting. |  | Recommendation paper expected to be submitted by the next meeting. | • Add the definition of “interconnector” to clause 1.5 of the HTR which refers to the PNR definition. • Replace all instances of “tie line” with interconnector. • Update HTR Table 2.10 to make appropriate use of definition for “interconnector” and “distribution feeders” as applicable. | Proceed to drafting. | See Status Update (10 July 2025)
| I42 | HTR 2.3.2e describes 'essential system services' to be put last for load shedding - however this is different to the defined essential system services ESS as defined in PNR. Similarly throughout the HTR "ancillary service" is used instead of "essential service" - the PNR and HTR should be aligned with this terminology to avoid confusion. | Low | Simple | Technical |  |  | - | Proposal to come to next meeting. |  | Closed. The WG suggests replacing the term "Ancillary Services" with "Essential System Services" | Replace the term of “ancillary services” with “essential services”.
Issue 44 | I44 | Definition of “back-up protection systems” for tie lines. Does this mean main & backup, or does this mean duplicate main protection. | Low | Simple | Technical | Noel (Rio) | James (ISO); David (HP); Nik (APA); Njabulo and Bec (BHP) | - | Proposal to come to next meeting. |  | No recommendations yet, suggestions sought from WG members. | Establish a subclause in clause 2.6.2 of the HTR which specifically deals with requirements of interconnectors, making reference to the nature and the role of tie line in the broader system, availability requirements of the tie line, and technical requirements for system stability. The focus should be away from forming a separate island. | Noel to check and reconvene group as required.
I2025.1 | I2025.1 | HTR 2.2.2(c) enables an NSP to agree alternative voltage targets with a controller for a point on the network. This may change the fundamental voltage operating standard for that part of the network for all future connections. It seems inappropriate for an NSP to have this power. | Moderate |  |  | Peter (ISO) | Nik (APA), Matthew (Rio) |  |  |  |  | n/a | New item. Group to discuss.
I2025.2 | I2025.2 | Review reactive power capability of inverter-based generating units, to ensure HTR requirements are technology agnostic as far as possible. | High |  |  | Nik (APA) | Peter (ISO), David (HP) |  |  |  |  | n/a | New item. Group to discuss.
I2025.3 | I2025.3 | HTR 3.3.4.4(e)(1)(A) needs to explicitly say that the increase in active power output must not be less than 5% of rated active power output. | Moderate |  |  | Peter (ISO) | - |  |  |  |  | n/a | New item. Proceed to drafting, and include in rule change consultation. | See Status Update (10 July 2025)
I2025.4 | I2025.4 | HTR 3.3.3.3(f) restricts reactive power absorption within 60 seconds of a fault. This no longer represents good industry practice. | High |  |  | Peter (ISO) | - |  |  |  |  | n/a | New item. ISO to provide memo for discussion at September meeting.
I2025.5 | I2025.5 | Clarify the use of ‘generating system’ and ‘generating unit’ for inverter-based generating facilities to meet the requirements of HTR. | Moderate |  |  | Peter (ISO) | - |  |  |  |  | n/a | New item. ISO to provide memo for discussion at September meeting.
I2025.6 | I2025.6 | Properly investigating power system incidents requires access to high speed data, and this will only become more true in future. The HTR do not currently require generators to have high speed data recorders. Requirements for facilities to have generator monitoring plans could cover this in part, and ISO powers to prescribe telemetry requirements may also provide a mechanism to require high speed data recording. To improve the situation, we first need to define the data that is needed, and then provide confidence that HTR requirements will make it available when needed. | High |  |  | Peter (ISO) | - |  |  |  |  | n/a | New item. To be discussed at August meeting. | Provide head of power for ISO to prescribe recorder requirements, with a transition period for existing facilities without recorders. Proceed to drafting, and include a consultation section in the exposure draft rules to discuss this issue and any others which are in the drafting but were not in the consultation paper.
I2025.7 | I2025.7 | The HTR definition of "point of common coupling" is specific to the Horizon Power network. This definition needs to be expanded to refer to any NSP. | Low |  |  | Peter (ISO) | - |  |  |  |  | n/a |  | Minor correction. Proceed to drafting.

## HTR - Closed Issues
EPNR Working Group - HTR Workstream Workbook
Issue ID |  | Description of Issue | Priority | Simple or Substantive | Governance or Technical | Lead | Support | Status Update (11 July) | Status Update (28 August) | Status Update (2 October 2024) | Status Update (10 October 2024) | Consultation Proposals (29 November 2024) | Notes
Issue 1 | I1 | NSP to NSP connection arrangements in the HTR and accountabilities. Right now the Rules only reference NSP to Applicant, which results in confusion when it is NSP to NSP connections via tie lines. | High | Simple | Governance | - | - | - |  |  |  | n/a | Out of HTR scope - governance issue.
Issue 2 | I2 | Equipment ratings and the cost of consumed ratings - how are costs managed when upgrades are necessary; whether the last project pays. | High | Simple | Governance | - | - | - |  |  |  | n/a | Out of HTR scope - governance issue.
Issue 20 | I20 | Improve definition of metering obligations for managing EBAS obligations. | High | Substantive | Governance | Jaden (HP) | - | - |  |  |  | n/a | Out of HTR scope - governance issue.
Issue 21 | I21 | How ESS costs are to be allocated (noting at the PAC Meeting 29.02.2024, the ISO advised that nominations would be called for a separate working group to be formed on this issue). | High | Substantive | Governance | - | - | - |  |  |  | n/a | Out of HTR scope - governance issue.
Issue 31 | I31 | Resolve responsibilities for determination of power transfer limits. | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP) | - | Proposal to come to next meeting. |  | Recommendation paper almost ready, to be circulated to WG. | NSPs will continue to be responsible for determining power transfer limit as they are best placed to determine this since they are responsible for networks and could understand overall network constraints the best. | No change required. Close 10 July 2025.
Issue 39 | I39 | Align with SWIS / other network operators. | n/a | n/a | n/a | - | - | - |  |  |  | n/a | Out of HTR scope - guiding principle
Issue 43 | I43 | Is accumulated synchronous time error still required? Has been removed from NEM. | Low | Simple | Technical | Peter (ISO) | Njabulo and Bec (BHP) | - | Proposal to come to next meeting. |  | WG members unsure how much equipment connected to the NWIS is still using electric clocks. NEM and WEM do not have time error measurement requirements. In absence of evidence of a need, consultation paper will recommend removal. | No changes to the PNR or HTR since providers of FCESS in the NWIS often rely on the standard for accumulated synchronous time error to determine effectiveness of the service. | No change required. Close 10 July 2025.
Issue 45 | I45 | Model guidelines and interaction of modelling guidelines with the HTR. How to ensure there are no mismatches in models. | Low | Simple | Technical | Noel (Rio) | James (ISO); Njabulo and Bec (BHP), Nik (APA) | - | The interim procedure published by the ISO may address these issues. Update at next meeting. |  | No recommendations yet, suggestions sought from WG members. | Item closed with no change necessary. | No change required. Close 10 July 2025.
Issue 46 | I46 | The existing Pilbara HTR offers disconnection as the primary means of dealing with non-compliance. There would be benefit for all parties if negotiation mechanisms were provided for that allow for re-testing and rectification of non-compliance without disconnection. This would enable parties to identify the causes of any performance issues and work together to solve them and continue operation where this is within acceptable risk limits given the unique non-compliance or performance issues. Sections in the Horizon Power TR A11.6 relate to these mechanisms where testing is concerned. Further work at both the Pilbara HTR and the various NSP TRs could be needed to achieve more optimal outcomes. | Low | Simple | Governance | - | - | - |  |  |  | n/a | Out of HTR scope - guiding principle