## 9 May Workshop Overview
Setting the Scene A primary goal of the EPNRWG's HTR Workstream is to ensure that the HTR provide a single minimum technical standard for generation and network equipment and expectation of technical performance for users on all interconnected networks in the Pilbara. Members have provided a list of existing issues and gaps in the HTR, which were compiled and provided to PAC on 18 April 2024. EPWA proposes that the issues in the long list can be categorised as 'governance' or 'technical', with governance framework items (including compliance and enforcement of standards, and change management of standards) are best suited to the PNR workstream; allowing this group to focus on technical issues related to minimum standards.
Today's workshop In conjunction with the ISO, EPWA has prepared for discussion (refer to tab Work Plan_Under Development): - A draft description of each issue - An indicative priority (High/Moderate/Low) for each issue - A preliminary assessment of the effort involved (simple or substantive) - Categorisation of issues as 'goverance' or 'technical' Outcomes sought from 9 May 2024 workstream meeting 1. Confirm intention for a single minimum standard for interconnected Pilbara networks 2. Agree governance issues to be addressed in PNR workstream, with this group (HTR workstream) to focus on the content of technical standards 3. Agree description of issue; indicative priority; effort involved for each of the 46 issues raised 4. Identify a responsible party(ies) to lead development of options for working group consideration
Future workstream meetings (11 July; 12 September; 14 November) Pending outcomes from 9 May meeting, the remaining three scheduled HTR workstream meetings will consider options for HTR issues raised. Depending on the issue: - the responsible party may develop a proposed solution, or may come up with initial options to bring back to the group for further discussions; or - it may be that issues are parked for inclusion as a piece of work to do on the implementation plan (to be published in February 2025).

## Work Plan_Under Development
OG # | Issue ID |  | Description of Issue | Priority | Simple or Substantive | Governance or Technical | Lead | Support | Current status
5 | I3 | I3 | Definition of contingency events versus credible contingency events and how this may flow on to pre-contingent events. The definition of credible contingency events currently doesn’t align with the AEMC definition which relates credible to things like weather conditions and present threats. | High | Substantive | Technical | Noel (Rio) | David (HP); Lekshmi (BP), Gemma (ISO); Njabulo and Bec (BHP) | This issue is being addressed by the review into Subchapters 7.3 and 7.4 of the PNR currently being conducted by the ISO. Interested parties can contribute to that review early by approaching the ISO directly, or by approaching Noel and group to consolidate inputs to the ISO.
22 |  | I36 | Requirements for generation to ride through multiple consecutive power system disturbances including minimum number of disturbances rode through within a specific period. | Moderate | Substantive | Technical |  |  | No considerable progress given it is substantive and technical. Consideration given to gather historical fault data to help determine the limits
9 | I4 |  | Consider requirements to update voltage and frequency standards in accordance with proposed legislative changes to voltage and frequency requirements. | High | Simple | Technical | David (HP) | Nik (APA); Njabulo and Bec (BHP); Noel (Rio), Gemma (ISO) | Recommended option: adopt standards in WEM regulations - outstanding issues: what is a low voltage connection (refer to papers for Item 5 at p16)
10 | I5 | I5 | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including review of the target frequency recovery times under Section 2.2.1 (25 minutes at 48 Hz) may have adverse impacts on system security. | High | Substantive | Technical | David (HP) | Nik (APA); Shervin and Scott (Woodside); Lekshmi (BP); Gemma (ISO); Njabulo and Bec (BHP); Noel (Rio) | Work has commenced on scoping the required modelling. The current expectation is that a first draft of the scoping of issues, and the work required for each issue, is to be presented at next meeting of the EPNRWG HTR Workstream.
|  | I6 | Frequency variations - do we need to lower the single contingency event limit due to increasing penetration of renewables / less system inertia e.g. NT has 47 Hz. | High | Substantive | Technical
33 |  | I15 | Currently requirement is for up to 4 Hz per second. This requirement has been updated in the WEM Rules. | High | Substantive | Technical
|  | I17 | Consider continuous uninterrupted operation requirements in section 3.3.3.3(h). It may not be prudent for the system if all generators follow this requirement simultaneously. Whilst a small system like NWIS might benefit from it, this needs to be confirmed with further studies. Also need to define the fault clearance time to comply to this requirement. This clause has been changed in the WEM Rules. Further, we note that some wind generators have not been able to meet this requirement. | High | Substantive | Technical
|  | I19 | The identified rate of response is difficult for some OEMs of non-dispatchable generating units to achieve – the current requirement is achieving 90% within 2 seconds and new output to be sustained for no more than 10 seconds. The minimum requirement of WEM rules (12.6) states asynchronous machines to meet 60% of the freq response in 6 seconds and 90% by 15 seconds. Related clauses in the WEM Rules to consider are: – A12.6.3.2 which provides more achievable requirements than the current Pilbara HTR. – A provision for negotiating the standard is requested. | High | Substantive | Technical
35 |  | I34 | ROCOF and include df/dt for under frequency load shedding and/or under frequency islanding. Determine if df/dt is used for islanding only, or if it can apply to ufls too. | Moderate | Substantive | Technical
18 | I7 |  | Consider requirements for NSPs to specify NWIS power system strength requirements and complete necessary assessments as renewable penetrations increases to ensure power system security. | High | Substantive | Goverance & Technical | Nik (APA) | Najbulo and Bec (BHP); Gemma (ISO); Noel (Rio); Lekshmi (BP) | Discussions have started but output not yet available.
23 | I8 | I8 | Consider wholistic review of the treatment of Battery Energy Storage Systems and inverter based generating units, including clarity on which sections of the rules apply for these generating units. | High | Substantive | Technical | Gemma (ISO) | David (HP); Noel (Rio); Njabulo and Bec (BHP), Nik (APA) | Project lead unavailable so work not commenced. Work to address this issue will commence to the extent practicable and, as appropriate, adopt analogous measures developed as part of the PSSR review.
24 |  | I9 | Reference to grid forming and grid following inverter technology may be helpful, with specific regard to the differences in the technical performance between the differing technologies. A definition here may be helpful as there doesn’t appear to be a clear definition on what is grid forming, grid following, or what has virtual synchronous generator performance. | High | Substantive | Technical
27 |  | I12 | Requirements for storage devices to provide network support services (frequency and voltage support) when operating in load/charging mode to enhance power system security/flexibility. Currently the HTR requires storage devices to act as consumer equipment when withdrawing power from the network. | High | Substantive | Technical
25 | I10 |  | Additional requirements for dynamic performance on asynchronous inverter connected generation e.g. damping capability for reactive power and active power control systems for inverter connected generation. | High | Substantive | Technical | Njabulo (BHP) | Nik (APA); David | Recommendation - New HTR Rules for generator requirements and obligations (refer to meeting papers for Item 5, at pp17-21). Updated paper with preferred option to be provided to the EPNRWG (HTR).
26 | I11 |  | Additional requirements for inverter connected generation response to power system disturbances, such as required magnitude of reactive current injection/absorption to support the power system during and post power system disturbances. | High | Substantive | Technical | Njabulo (BHP) | Nik (APA); David
31 | I13 | I13 | Definition and use of 'energisation' vs 'commercial operations' is inconsistent throughout the HTR and PNR. Clarity is required about the process and what actions are required from each party at which stage. Inclusion of data to be submitted with connection applications (See Horizon Power Tech Rules Sections 3.3.2, 3.4.3, 3.6.5, and Attachments 3-10). | High | Substantive | Governance & Technical | Gemma (ISO) | David (HP); Njabulo and Bec (BHP), Nik (APA) | Work in progress - Proposed solution/recommendation to EPNRWG to be provided in advance of next WS2 meeting.
41 |  | I37 | Inclusion of Testing requirements and test details for connection of Generating Units (See Horizon Power Tech Rules Attachment 11). Dispatchable and non-dispatchable generator testing and compliance requirements and R2 model validation. What are the non-dispatchable unit testing requirements, and how does this differ to dispatchable units. | Moderate | Substantive | Technical
32 | I14 |  | Renewable generation could comply, but the requirement of 460 ms ride through is overly onerous. We suggest this is revisited system wide to test suitability given it is inconsistent with other countries. The interpretation of the wording should be clarified as it is not clear if this a requirement or optional (Western Power historically tested compliance with this an equivalent clause with some flexibility in the interpretation). | High | Substantive | Technical | Lekshmi (BP) | Gemma (ISO); Njabulo and Bec (BHP);Nik (APA) | Work started - to be workshopped with issue team in next 2 weeks and proposal developed by end of July 2024 (ditto for I18)
34 | I16 |  | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: - Review Section 3.3.3.3(f) - Absorption of reactive power is helpful under some circumstances and may be required for longer periods. Review clause in context of new operating environment. - Most OEMs struggle to achieve the requirement for any pre-fault absorption of reactive power to be terminated within 200 ms after clearing of the fault. Further, from a system perspective, it would not be optimal if all generators stop absorbing after 200 ms. - The WEM Rules have changed this clause (as did the proposed updated to the WP TR). | High | Substantive | Technical | David (HP) | Gemma (ISO); Njabulo and Bec (BHP); Noel (Rio), Nik (APA) | Issue I16 to be bundled with I5 issues requiring further studies.
37 | I18 |  | This is currently 0.05 Hz. The point at which the dead band is measured is unclear in the current drafting and needs to be updated. The WEM Rules have been revised to be +/-0.025 Hz around 50.0 Hz (refer to A12.6.1.9). | High | Simple | Technical | Lekshmi (BP) | Njabulo and Bec (BHP) | Work started - to be workshopped with issue team in next 2 weeks and proposal developed by end of July 2024 (ditto for I14)
20 | I22 |  | Consider requirements regarding disturbance monitoring and synchrophasors. | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP); Noel (Rio), Nik (APA) | No update
28 | I23 |  | Consider update to Figure 3.3 noting the four-quadrant capability of inverters. | Moderate | Simple | Technical | David (HP) | Nik (APA); Njabulo and Bec (BHP) | No update
29 | I24 | I24 | Clarify treatment of ambient temperatures in the context of Section 3.3.3.1. Clarify distinction of using ‘nameplate’ vs ‘derated capacity’ when determining which set of generator compliance rules should apply. | Moderate | Simple | Technical | David (HP) | Lekshmi (BP); Njabulo and Bec (BHP); Noel (Rio), Nik (APA), Gemma (ISO) | No update
30 |  | I25 | The temperature dependency is a critical factor in the Pilbara that is not adequately considered in the Pilbara HTR. The higher temperatures in the Pilbara will affect the generator’s ability to comply with maximum output requirements (or the maximum output that can be expected). Reactive power related requirements are linked to temperature, whereas historical versions of the rules including the current Pilbara HTR have not linked active power to temperature. This issue should be resolved in the Pilbara HTR to allow the network operator to have a more realistic understanding of what the generation is able to and expected to achieve. In the WEM, wind farms struggle to meet the reactive power capability requirements at 40 degrees (for example A12.2.3.2). However, WEM Rules are more realistic where consideration of temperature is concerned. Of note: – Reactive power capability in clause 3.3.3.1 on possible map with locations and ambient temperature. – Active power capability might need to be de-rated for the wind and solar farms above certain temperatures. This may be a gap in the existing Pilbara HTR as we were unable to identify the relevant clause. – Recommend a review of clauses that refer to “ambient temperature” in addition to the above to ensure suitability. | Moderate | Simple | Technical |  |  | No update
36 | I26 |  | Inclusion of Monitoring and Control Requirements (See Horizon Power Tech Rules Section 3.3.4). | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP), Nik (APA) | -
40 | I27 |  | Consider requirements for pole slip protection, e.g. where Critical Fault Clearance time issues exist. | Moderate | Simple | Technical | Nik (APA) | David (HP); Gemma (ISO); Njabulo and Bec (BHP); Noel (Rio) | Meeting held with Njabulo Mlilo & David Stephens on 06/06/24. Agreement was to propose a set of minimum requirements for generating unit protection, aligned with rating, location and technology. Nik Walker to issue summary of meeting.
44 | I28 |  | Review of fault level management on the system: - Consider minimum fault rating requirements for Transmission plant at significant network nodes, and fault level management. - Consider potential requirements for limitations on maximum fault levels on the system and consider providing guidance on the calculation of fault levels. Define credible versus ultimate case. | High | Substantive | Technical | David (HP) | Noel (Rio); Gemma (ISO); Njabulo and Bec (BHP), Nik (APA) | Discussions scheduled in 2 weeks on how multiple network operators manage fault levels at the point of interconnection. A call is open for expressions of interest in assisting David with this issue.
1 | I29 |  | Consider requirements adequacy of black start requirements/arrangements. | High | Substantive (study likely) | Technical | Gemma (ISO) | David (HP); Njabulo and Bec (BHP) | To be combined with other changes to the Protocol Framework Procedure arising out of ISO review of Subchapters 7.3 and 7.4 of the PNR. Any issues outstanding after this are to be further discussed in this working group.
2 | I30 |  | Connection Point Compliance parameters and definition (including negotiated vs ideal rules - with particular consideration for brownfield plant vs greenfield). Consider if any updates required to facilitate or improved the treatment of Connection Point Compliance measures. | High | Substantive | Governance & Technical | Shervin and Scott (Woodside) | David (HP); Noel (Rio); Njabulo and Bec (BHP), Nik (APA), Gemma (ISO) | Recommend no change to HTR so changes to CPC arrangements in PNR are not invalidated. Review access and connection procedure and identify any deficiencies (if there are any) but make reference to the PNR and to heads of power within the HTR.
13 | I31 |  | Resolve responsibilities for determination of power transfer limits. | Moderate | Simple | Technical | David (HP) | Njabulo and Bec (BHP) | No update
15 | I32 | I32 | Update Critical Fault Clearing Times at Dampier and Cape Lambert 33kV to reflect recent system changes and approved derogations. | Moderate | Substantive (study likely) | Technical | Gemma (ISO) | Noel (Rio); David (HP); Njabulo and Bec (BHP), Nik (APA) | -
16 |  | I33 | Overall review of visit of maximum fault clearance times to ensure alignment. Currently there is misalignment between Western Power, Horizon Power and Rio Tinto technical rules. | Moderate | Substantive (study likely) | Technical |  |  | -
21 | I35 |  | Requirements on NSPs to enact special protection schemes to manage network congestion/instability as required to enhance system security. However, this shouldn’t be the sole option to manage security issues – network augmentation and re-dispatch are other methods by which this can be achieved. Generators and loads to possess compliant control systems to facilitate operation of required network special protection schemes to be specified in connection agreements. | Moderate | Substantive | Technical | Njabulo (BHP) | - | A call is open for expressions of interest in assisting Njabulo with this issue.
42 | I38 |  | Requirements for NSP to verify integrity of the UFLS scheme across the NWIS network via periodic tests and publish an annual performance report based test results and actual power system UFLS events, this will provide confidence to all customers of UFLS performance integrity and power system security. | Moderate | Substantive | Technical | Njabulo (BHP) | Shervin and Scott (Woodside) | Recommended option: Self-regulation option (refer to meeting papers for Item 5 at pp22-25); Regarding the role of the ISO in post-incident investigations, additional rules should be drafted allowing the ISO to provide additional guidance, and participants to report on how they meet requirements on an annual basis.
4 | I40 |  | Overall review of referenced standards, noting that some standards have more recent versions than those referenced. | Low | Simple | Technical | David (HP) | Njabulo and Bec (BHP) | No update
6 | I41 | I41 | Better clarity required for definitions of distribution feeder / interconnector / tie (undefined but included in HTR Table 2.10). | Low | Simple | Technical | Gemma (ISO) | Noel (Rio); Njabulo and Bec (BHP), Nik (APA) | -
7 |  | I42 | HTR 2.3.2e describes 'essential system services' to be put last for load shedding - however this is different to the defined essential system services ESS as defined in PNR. Similarly throughout the HTR "ancillary service" is used instead of "essential service" - the PNR and HTR should be aligned with this terminology to avoid confusion. | Low | Simple | Technical |  |  | -
12 | I43 |  | Is accumulated synchronous time error still required? Has been removed from NEM. | Low | Simple | Technical | Gemma (ISO) | Njabulo and Bec (BHP) | -
14 | I44 |  | Definition of “back-up protection systems” for tie lines. Does this mean main & backup, or does this mean duplicate main protection. | Low | Simple | Technical | Noel (Rio) | Gemma (ISO); David (HP); Nik (APA); Njabulo and Bec (BHP) | No update
| I45 |  | Model guidelines and interaction of modelling guidelines with the HTR. How to ensure there are no mismatches in models. | Low | Simple | Technical | Noel (Rio) | Gemma (ISO); Njabulo and Bec (BHP), Nik (APA) | No update
| I1 |  | NSP to NSP connection arrangements in the HTR and accountabilities. Right now the Rules only reference NSP to Applicant, which results in confusion when it is NSP to NSP connections via tie lines. | High | Simple | Governance |  |  | -
| I2 |  | Equipment ratings and the cost of consumed ratings - how are costs managed when upgrades are necessary; whether the last project pays. | High | Simple | Governance |  |  | -
| I20 |  | Improve definition of metering obligations for managing EBAS obligations. | High | Substantive | Governance | Jaden (HP) |  | -
39 | I21 |  | How ESS costs are to be allocated (noting at the PAC Meeting 29.02.2024, the ISO advised that nominations would be called for a separate working group to be formed on this issue). | High | Substantive | Governance |  |  | -
43 | I46 |  | The existing Pilbara HTR offers disconnection as the primary means of dealing with non-compliance. There would be benefit for all parties if negotiation mechanisms were provided for that allow for re-testing and rectification of non-compliance without disconnection. This would enable parties to identify the causes of any performance issues and work together to solve them and continue operation where this is within acceptable risk limits given the unique non-compliance or performance issues. Sections in the Horizon Power TR A11.6 relate to these mechanisms where testing is concerned. Further work at both the Pilbara HTR and the various NSP TRs could be needed to achieve more optimal outcomes. | Low | Simple | Governance |  |  | -
3 | I39 |  | Align with SWIS / other network operators. | n/a | n/a | n/a |  |  | -

## Initial Submissions Received
OG # | Consolidated Issue # | Rule | Topic | Description of Issue | Submitter
8 | 1 | 1.8.1(b) | Interconnection points | NSP to NSP connection arrangements in the HTR and accountabilities. Right now the Rules only reference NSP to Applicant, which results in confusion when it is NSP to NSP connections via tie lines. | Rio Tinto
19 | 2 | 3.2.1(f) | Cost of upgrades | This may not fall into the HTR, but it relates to equipment ratings and the cost of consumed ratings. How are costs managed when upgrades are necessary, does the last project pay? | Rio Tinto
5 | 3 | 1.5 | Definitions | Definition of contingency events versus credible contingency events and how this may flow on to pre-contingent events. The definition of credible contingency events currently doesn’t align with the AEMC definition which relates credible to things like weather conditions and present threats. | Rio Tinto
9 | 4 | 2.2 | Power system performance standards | Consider requirements to update voltage and frequency standards in accordance with proposed legislative changes to voltage and frequency requirements. | Horizon Power
10 | 5 | 2.2.1 | Power system performance standards | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: Review the target frequency recovery times under Section 2.2.1 - 25 minutes at 48 Hz may have adverse impacts on system security. | Horizon Power
11 | 6 | 2.2.1 | Power system performance standards | Frequency variations - do we need to lower the single contingency event limit due to increasing penetration of renewables / less system inertia e.g. NT has 47 Hz | ISO
18 | 7 | 3 | System strength | Include system strength assessments into the HTR and associated guidance on how to do that. | Rio Tinto
18 | 7 | 3 | System strength | Requirements for NSPs to specify NWIS power system strength requirements and complete necessary assessments as renewable penetrations increases to ensure power system security. | BHP
18 | 7 | 3 | System strength | System strength assessment and remediation requirements | ISO
23 | 8 | 3.3 | Inverter generating units | Consider wholistic review of the treatment of Battery Energy Storage Systems and inverter based generating units, including clarity on which sections of the rules apply for these generating units. | Horizon Power
23 | 8 | 3.3 | Inverter generating units | Applicability of this section to BESS | ISO
23 | 8 | 3.7 | New Connections | Requirements for connection of storage facilities | ISO
24 | 9 | 3.3 | Inverter generating units | Reference to grid forming and grid following inverter technology may be helpful, with specific regard to the differences in the technical performance between the differing technologies. A definition here may be helpful as there doesn’t appear to be a clear definition on what is grid forming, grid following, or what has virtual synchronous generator performance. | Rio Tinto
25 | 10 | 3.3 | Inverter generating units | Additional requirements for dynamic performance on asynchronous inverter connected generation e.g. damping capability for reactive power and active power control systems for inverter connected generation. | BHP
26 | 11 | 3.3 | Inverter generating units | Additional requirements for inverter connected generation response to power system disturbances, such as required magnitude of reactive current injection/absorption to support the power system during and post power system disturbances. | BHP
26 | 11 | 3.6.7 | Power factor requirements | Load power factor requirements | ISO
27 | 12 | 3.3 | Inverter generating units | Requirements for storage devices to provide network support services (frequency and voltage support) when operating in load/charging mode to enhance power system security/flexibility. Currently the HTR requires storage devices to act as consumer equipment when withdrawing power from the network. | BHP
31 | 13 | 3.3.2, 3.4.3, 3.6.5, Attachments | New Connections | Inclusion of data to be submitted with connection applications (See Horizon Power Tech Rules Sections 3.3.2, 3.4.3, 3.6.5, and Attachments 3-10). | Horizon Power
31 | 13 | 4.1.3 / 4.2.5 / Attachment 11 & 12 PNR 255, 269, 270, 274D, 274H | New Connections | Definition and use of 'energisation' vs 'commercial operations' is inconsistent throughout the HTR and PNR. Clarity is required about the process and what actions are required from each party at which stage. | ISO
32 | 14 | 3.3.3.3(c) | Immunity to voltage excursions | Renewable generation could comply, but the requirement of 460 ms ride through is overly onerous. We suggest this is revisited system wide to test suitability given it is inconsistent with other countries. The interpretation of the wording should be clarified as it is not clear if this a requirement or optional (Western Power historically tested compliance with this an equivalent clause with some flexibility in the interpretation). | BP
33 | 15 | 3.3.3.3(d) | ROCOF | Currently requirement is for up to 4 Hz per second. However, a requirement of up to 1 to 2 Hz is more realistic. This requirement has been updated in the WEM Rules. In A12.7.3.2, the minimum requirements are reasonable and requires a RoCoF to: – reach 2 Hz/s over 250 milliseconds during the disturbance, or – reach 1 Hz/s over 1 second during the disturbance. Subject to further studies with the new renewables in service the exact number (1 to 2 Hz) could be clarified and rationale for what is achievable identified. | BP
33 | 15 | 3.3.3.3(d) | ROCOF | ROCOF - 4 Hz/s | ISO
34 | 16 | 3.3.3.3(f) | Post-fault reactive power of a power station with non-synchronous generating units | Most OEMs struggle to achieve the requirement for any pre-fault absorption of reactive power to be terminated within 200 ms after clearing of the fault. Further, from a system perspective, it would not be optimal if all generators stop absorbing after 200 ms. The WEM Rules have changed this clause (as did the proposed updated to the WP TR). The new clause in A12.9 is more appropriate. | BP
34 | 16 | 3.3.3.3(f) | Post-fault reactive power of a power station with non-synchronous generating units | Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: Review Section 3.3.3.3(f) - Absorption of reactive power is helpful under some circumstances and may be required for longer periods. Review clause in context of new operating environment. | Horizon Power
35 | 17 | 3.3.3.3(h) | Continuous uninterrupted operation | It is not prudent for the system if all generators follow this requirement simultaneously. This clause has been changed in the WEM Rules. Further, we note that some wind generators have not been able to meet this requirement. | BP
37 | 18 | 3.3.4.4(d) | Dead band | This is currently 0.05 Hz. The point at which the dead band is measured is unclear in the current drafting and needs to be updated. The WEM Rules have been revised to be +/-0.025 Hz around 50.0 Hz (refer to A12.6.1.9). | BP
38 | 19 | 3.3.4.4(f) | Rate of response | The identified rate of response is difficult for some OEMs of non-dispatchable generating units to achieve – the current requirement is achieving 90% within 2 seconds and new output to be sustained for no more than 10 seconds. The minimum requirement of WEM rules (12.6) states asynchronous machines to meet 60% of the freq response in 6 seconds and 90% by 15 seconds. Related clauses in the WEM Rules to consider are: – A12.6.3.2 which provides more achievable requirements than the current Pilbara HTR. – A provision for negotiating the standard is requested. | BP
45 | 20 | PNR 138 | Metering | Improve definition of metering obligations for managing EBAS obligations | Horizon Power
46 | 21 | PNR Chapter 8 | ESS Costs | How ESS costs are to be allocated (noting at the PAC Meeting 29.02.2024, the ISO advised that nominations would be called for a separate working group to be formed on this issue) | Rio Tinto
20 | 22 | 3.2.3 | Disturbance Monitoring | Consider requirements regarding disturbance monitoring and synchrophasors. | Horizon Power
28 | 23 | 3.3 | Inverter generating units | Consider update to Figure 3.3 noting the four-quadrant capability of inverters. | Horizon Power
29 | 24 | 3.3.3.1 | Temperature dependency | Clarify treatment of ambient temperatures in the context of Section 3.3.3.1. Clarify distinction of using ‘nameplate’ vs ‘derated capacity’ when determining which set of generator compliance rules should apply. | Horizon Power
30 | 25 | 3.3.3.1 (reactive power capability), various others | Temperature dependency | The temperature dependency is a critical factor in the Pilbara that is not adequately considered in the Pilbara HTR. The higher temperatures in the Pilbara will affect the generator’s ability to comply with maximum output requirements (or the maximum output that can be expected). Reactive power related requirements are linked to temperature, whereas historical versions of the rules including the current Pilbara HTR have not linked active power to temperature. This issue should be resolved in the Pilbara HTR to allow the network operator to have a more realistic understanding of what the generation is able to and expected to achieve. In the WEM, wind farms struggle to meet the reactive power capability requirements at 40 degrees (for example A12.2.3.2). However, WEM Rules are more realistic where consideration of temperature is concerned. Of note: – Reactive power capability in clause 3.3.3.1 on possible map with locations and ambient temperature. – Active power capability might need to be de-rated for the wind and solar farms above certain temperatures. This may be a gap in the existing Pilbara HTR as we were unable to identify the relevant clause. – Recommend a review of clauses that refer to “ambient temperature” in addition to the above to ensure suitability. | BP
36 | 26 | 3.3.4 | Monitoring and Control Requirements | Inclusion of Monitoring and Control Requirements (See Horizon Power Tech Rules Section 3.3.4). | Horizon Power
40 | 27 | 3.4.10.2 | Pole slip | Consider requirements for pole slip protection, e.g. where critical fault clearance time (CFCT) issues exist. | Horizon Power
44 | 28 | 5.4.1 | Power System Fault Levels | Fault level credible scenarios, definition of what is credible versus ultimate case. This relates to equipment rating, and can relate to 100% generation being online and running when that is not a scenario that is possible. This relates to max fault current contribution calculation method for equipment rating and its methodology. | Rio Tinto
44 | 28 | 5.4.1 | Power System Fault Levels | Review of fault level management on the system: Consider minimum fault rating requirements for Transmission plant at significant network nodes, and fault level management. Consider potential requirements for limitations on maximum fault levels on the system and consider providing guidance on the calculation of fault levels. | Horizon Power
1 | 29 | - | Black Start | Consider requirements adequacy of black start requirements/arrangements. | Horizon Power
2 | 30 | - | Connection Point Compliance | Connection Point Compliance parameters and definition (including negotiated vs ideal rules - with particular consideration for brownfield plant vs greenfield) | Rio Tinto
2 | 30 | - | Connection Point Compliance | Consider if any updates required to facilitate or improved the treatment of Connection Point Compliance measures. | Horizon Power
13 | 31 | 2.3.7, 2.3.8 | Power transfer limits | Resolve responsibilities for determination of power transfer limits (Sections 2.3.7 - 2.3.8) | Horizon Power
15 | 32 | 2.6.4 | Maximum total fault clearance times | Maximum total fault clearance times for 33kV tie lines are incorrect. Previous study suggested 365ms is the correct value, though some recent studies were carried out between HP and RTIO on this. | Rio Tinto
15 | 32 | 2.6.4 | Maximum total fault clearance times | Update Critical Fault clearing times at Dampier and Cape Lambert 33kV to reflect recent system changes and approved derogations. | Horizon Power
15 | 32 | 2.6.4 | Maximum total fault clearance times | Maximum fault clearing time for HP-RTIO tie line | ISO
16 | 33 | 2.6.4 | Maximum total fault clearance times | Overall review of visit of maximum fault clearance times (CFCT’s) to ensure alignment. Currently there is misalignment between Western Power, Horizon Power and Rio Tinto technical rules. | Rio Tinto
17 | 34 | 2.4 | ROCOF | ROCOF and include df/dt for under frequency load shedding and/or under frequency islanding. Determine if df/dt is used for islanding only, or can this apply to ufls too? | Rio Tinto
21 | 35 | 3.2.6 (b) | Protection | Requirements on NSPs to enact special protection schemes to manage network congestion/instability as required to enhance system security. However, this shouldn’t be the sole option to manage security issues – network augmentation and re-dispatch are other methods by which this can be achieved. Generators and loads to possess compliant control systems to facilitate operation of required network special protection schemes to be specified in connection agreements. | BHP
22 | 36 | 3.3 | Generation ride through | Requirements for generation to ride through multiple consecutive power system disturbances including minimum number of disturbances rode through within a specific period. | BHP
41 | 37 | 4 | Testing | Dispatchable and non-dispatchable generator testing and compliance requirements and R2 model validation. What are the non-dispatchable unit testing requirements, and how does this differ to dispatchable units. | Rio Tinto
41 | 37 | Attachment 11 | Testing | Inclusion of Testing requirements and test details for connection of Generating Units (See Horizon Power Tech Rules Attachment 11). | Horizon Power
42 | 38 | 4 | Testing | Requirements for NSP to verify integrity of the UFLS scheme across the NWIS network via periodic tests and publish an annual performance report based test results and actual power system UFLS events, this will provide confidence to all customers of UFLS performance integrity and power system security. | BHP
3 | 39 | - | Rules Alignment | If there is opportunity for aligning the various N.O. Technical Rules into common for users. | Rio Tinto
3 | 39 | - | Rules Alignment | Alignment of the HTR with the SWIS technical rules. | Rio Tinto
4 | 40 | - | Standard references | Consider update of flicker, harmonics, and power quality standards to latest version of relevant standards i.e. AS/NZS 61000.3. | Horizon Power
4 | 40 | - | Standard references | Overall review of referenced standards, noting that some standards have more recent versions than those referenced. | Horizon Power
6 | 41 | 1.5 | Definitions | Interconnection definition in the Rules currently refers to transmission lines, however a tie line isn’t necessary considered as a transmission line. Refining this definition with regard to 33kV tie lines will provide more clarity. | Rio Tinto
6 | 41 | 1.5 | Definitions | Better clarity required for definitions of distribution feeder / interconnector / tie (undefined but included in HTR Table 2.10). | ISO
7 | 42 | 1.5 | Definitions | HTR 2.3.2e Describes 'essential system services' to be put last for load shedding - however this is different to the defined essential system services ESS as defined in PNR. Similarly throughout the HTR "ancillary service" is used instead of "essential service" - the PNR and HTR should be aligned with this terminology to avoid confusion. | ISO
12 | 43 | 2.2.1b | Power system performance standards | Is accumulated synchronous time error still required? Has been removed from NEM | ISO
14 | 44 | 2.6.2, Definitions | Protection | Definition of “back-up protection systems” for tie lines. Does this mean main & backup, or does this mean duplicate main protection. | Rio Tinto
39 | 45 | 3.3.9, 3.6.12 | Model | Model guidelines and interaction of modelling guidelines with the HTR. How to ensure there are no mismatches in models. | Rio Tinto
43 | 46 | 4 / potential new section | Flexibility to negotiate when issues are identified post-testing | The existing Pilbara HTR offers disconnection as the primary means of dealing with non-compliance. There would be benefit for all parties if negotiation mechanisms were provided for that allow for re-testing and rectification of non-compliance without disconnection. This would enable parties to identify the causes of any performance issues and work together to solve them and continue operation where this is within acceptable risk limits given the unique non-compliance or performance issues. Sections in the Horizon Power TR A11.6 relate to these mechanisms where testing is concerned. Further work at both the Pilbara HTR and the various NSP TRs could be needed to achieve more optimal outcomes. | BP