## Cover
Public Utilities Office
Modelling the impacts of constrained access
Wednesday 28 February
Reliance Restricted

## Notice
Ernst & Young (“we” or “EY”) has been engaged by the Public Utilities Office (“you”, “PUO” or the “Client”) to provide electricity market modelling services to assist the PUO in investigating the relative financial impacts of implementing a constrained network access regime on existing and new generators in the Wholesale Electricity Market (the “Services”), in accordance with our Letter of Appointment dated 21 November 2017 and the Panel Contract.
The enclosed report (the “Report”) sets out the modelling methodologies and key data inputs and assumptions to be used in delivering the Services. The methodology described, together with the scenarios and assumptions used, will form the basis for the outputs produced and either have been, or will be, agreed with the PUO, following the end of this public consultation process and after due consideration of the submissions received.
The Report should be read in its entirety including the applicable scope of the work and any limitations. A reference to the Report includes any part of the Report. The report has been constructed based on information current as of 28 February 2018 (being the date of completion of this Report), and which has been provided by the Client, other stakeholders or is available publically. Since this date, material events may have occurred that are not reflected in the report.
EY has prepared the Report for the benefit of the PUO and has considered only the interests of the PUO. EY has not been engaged to act, and has not acted, as advisor to any other party. Accordingly, EY makes no representations as to the appropriateness, accuracy or completeness of the Report for any other party's purposes.
No reliance may be placed upon the Report or any of its contents by any recipient of the Report for any purpose and any party receiving a copy of the Report must make and rely on their own enquiries in relation to the issues to which the Report relates, the contents of the Report and all matters arising from or relating to or in any way connected with the Report or its contents.
EY disclaims all responsibility to any other party for any loss or liability that the other party may suffer or incur arising from or relating to or in any way connected with the contents of the Report, the provision of the Report to the other party or the reliance upon the Report by the other party.
No claim or demand or any actions or proceedings may be brought against EY arising from or connected with the contents of the Report or the provision of the Report to any party. EY will be released and forever discharged from any such claims, demands, actions or proceedings.
Our methodologies chosen are based, in part, on the assumptions stated and on information provided by the stakeholders engaged in this process. We do not imply, and it should not be construed that we have performed audit or due diligence procedures on any of the information provided to us. We have not independently verified, or accept any responsibility or liability for independently verifying, any such information nor do we make any representation as to the accuracy or completeness of the information. We accept no liability for any loss or damage, which may result from your reliance on any research, analyses or information so supplied.
Modelling work performed as part of our scope inherently requires assumptions about future behaviours and market interactions, which may result in forecasts that deviate from future conditions. There will usually be differences between estimated and actual results, because events and circumstances frequently do not occur as expected, and those differences may be material.
EY have consented to the Report being published electronically on the PUO website for the purpose of undertaking a public consultation. EY have not consented to distribution or disclosure beyond this. The material contained in the Report, including the EY logo, is copyright and copyright in the Report itself vests in the PUO. The Report, including the EY logo, cannot be altered without prior written permission from EY.
EY’s liability is limited by a scheme approved under Professional Standards Legislation.

## Welcome
Public Utilities Office
Input assumptions book
Notice
This workbook should be read in conjunction with the consultation paper for modelling the impact of constrained access.
This workbook is subject to the terms and conditions of the notice governing the consultation paper.
Purpose
This assumptions book illustrates the quantitative assumptions that are proposed to be used by EY for the constrained access modelling for the PUO.
The worksheets in this book provide the assumptions for each driver for each scenario.
Associated sources for each data set are outlined in each worksheet along with the real dollar value of any costs - all dollar values in this workbook are real June 2017 dollars unless otherwise stated.
How to navigate this assumptions book
The Scenarios tab in this workbook contains some key study parameters and summarises the assumptions for each scenario.
The subsequent tabs contain the detailed data behind each set of assumptions, with other input data used in the model.
All cells with coloured numbers represent calculations. All data with no colours are the numbers taken directly from the data source.
Date | Version | Notes
2018-02-28 | 1 | Workbook created for publishing as part of the consultation.

## Scenarios
Key drivers for selection
Study start: | 2022-07-01
Study end: | 2032-06-30
Number of years: | 10
Reporting dollars: | real June 2017 AUD
| Scenario name | Scenario narrative
| Base Scenario | Business as usual, using AEMO's Neutral economic growth assumptions and without any emissions reduction policy post 2020.
| Low demand | As in Base Scenario, except using AEMO's Weak economic growth assumptions. This will test the bookend on constrained access outcomes in a future with low demand.
| High demand | As in Base Scenario, except using AEMO's Strong economic growth assumptions. This will test the bookend on constrained access outcomes in a future with high demand.
Key driver | Sheet | Options | Base Scenario | Low demand | High demand
Emission reduction policy | Carbon price | 1. No emissions reduction policy post 2020. 2. Carbon price. If carbon pricing returns (we consider 2020-21 at the earliest), trajectories include: 2a AEMO NEFR 2016 Neutral trajectory 2b. AEMO NEFR 2015 Moderate Trajectory 3. National emissions reduction policy without explicit carbon price. a. WEM achieves pro-rata emissions target of Paris agreement by 2030, estimated to be 8.4 MT CO2-e. b. WEM achieves deep emissions cuts by 2030: 6 MT CO2-e. | Option 1 | Option 1 | Option 1
Renewable energy targets | N/A | 1. Legislated LRET (33 TWh by 2020) 2. Legislated LRET (33 TWh by 2020) plus WA state-based target | Option 1 | Option 1 | Option 1
New renewable generation | SWIS renewable planting list | 1. Suggested initial expansion plan provided in SWIS renewable planting list based on advanced generator connections. 2. Alternative plan, which could be requested by the Client. [Note: Additional renewable projects are planted throughout the study in response to market conditions] | Option 1 | Option 1 | Option 1
Thermal generation retirements | Generator retirements | 1. Synergy 380 MW base retirement schedule 2. Synergy 380 MW base retirement schedule with additional Client specified retirement [Note: Additional projects may be retired throughout the study in response to market conditions] | Option 1 | Option 1 | Option 1
Energy | Energy Forecasts Peak Demand Forecasts | 1. AEMO ESOO 2017 (published in June 2017) - Expected 2. AEMO ESOO 2017 (published in June 2017) - High 3. AEMO ESOO 2017 (published in June 2017) - Low 4. AEMO ESOO 2017 (published in June 2017) - Low, with additional industrial and edge-of-grid loads moving off-grid | Option 1 | Option 3 | Option 2
Rooftop PV | Rooftop PV | 1. AEMO ESOO 2017 (published in June 2017) - Expected 2. AEMO ESOO 2017 (published in June 2017) - High 3. AEMO ESOO 2017 (published in June 2017) - Low 4. Higher rooftop PV uptake than High ESOO 2017 scenario | Option 1 | Option 3 | Option 2
Behind-the-meter storage uptake | Battery storage forecasts | 1. AEMO ESOO 2017 (published in June 2017) - Expected 2. AEMO ESOO 2017 (published in June 2017) - High 3. AEMO ESOO 2017 (published in June 2017) - Low 4. Based on AEMO ESOO 2017 (published in June 2017) - Higher uptake | Option 1 | Option 3 | Option 2
Electric vehicles | Electric vehicles | 1. AEMO ESOO 2017 (published in June 2017) - Expected 2. AEMO ESOO 2017 (published in June 2017) - High 3. AEMO ESOO 2017 (published in June 2017) - Low 4. Higher EV uptake than High ESOO 2017 scenario | Option 1 | Option 3 | Option 2
Industrial demand | N/A | 1. No change - just as per AEMO ESOO 2017 trajectory 2. Client specified industrial load changes | Option 1 | Option 1 | Option 1
Transmission network expansion | N/A | 1. Reflected in the constraint equations provided by Western Power. | Option 1 | Option 1 | Option 1
Fuel prices | Fuel prices GSOO Fuel prices existing units | 1. AEMO GSOO 2016 Base fuel price trajectory. 2. AEMO GSOO 2016 High fuel price trajectory. 3. AEMO GSOO 2016 Low fuel price trajectory. | Option 1 | Option 1 | Option 1
New entrant parameters | New entrant params | 1. AEMO NTNDP 2016 | Option 1 | Option 1 | Option 1
Technology CAPEX | Capex | 1. AEMO NTNDP 2016, plus CSIRO/Jacobs 2016 storage capex Neutral trajectory 2. AEMO NTNDP 2016 with adjustments to wind and solar in early years in line with recent public announcements, plus CSIRO/Jacobs 2016 storage capex Neutral trajectory 3. AEMO NTNDP 2016 with adjustments to wind, solar and storage in line with recent public announcements | Option 2 | Option 2 | Option 2
Demand response | N/A | 1. 106 MW total DSM capacity to be modelled for duration of study, as per 2017-18 capacity credits. This demand response is modelled explicitly in the simulation responding to high prices as a last resort. | Option 1 | Option 1 | Option 1
WACC | WACC Aug 15 | 1. Pre-tax, real WACC of 7.5% from IPART Aug 15 data, adjusted for higher gearing ratio 2. Higher WACC to represent investment uncertainty. | Option 1 | Option 1 | Option 1
Renewable bidding strategy | N/A | 1. Renewable projects to be bid at $0/MWh. 2. Renewable projects built before 2020 to be bid at -$40/MWh to reflect implicit LGC revenue. Other projects to be bid at $0/MWh. | Option 1 | Option 1 | Option 1
Generator marginal loss factors | MLFs | 1. As provided by the PUO for the Southern Terminal reference node. | Option 1 | Option 1 | Option 1

## Carbon price
Carbon price
Real June 2017 AUD/tonne CO2-e
Source, AEMO "Moderate": AEMO Planning Assumptions (2015)
Source, AEMO "Neutral": Retail electricity price history and projections (2016). https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/-/media/E32734E08CD54504B2A5F408FAAB1870.ashx
;Carbon price ($/t CO2-e) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48
_ | AEMO "Moderate" 2015 | 0 | 0 | 0 | 0 | 0 | 10.9982 | 11.3142 | 11.6608 | 12.0074 | 12.3743 | 12.782 | 13.2407 | 13.7198 | 14.209 | 14.7289 | 15.2589 | 15.8195 | 16.4107 | 17.0223 | 17.6747 | 18.3372 | 19.0507 | 19.7846 | 20.5389 | 21.1199 | 21.7111 | 22.2819 | 22.8527 | 23.3929 | 23.9128 | 24.3918 | 24.3918
_ | No explicit carbon price | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
_ | AEMO "Neutral" 2016 | 0 | 0 | 0 | 0 | 25.5946 | 28.1541 | 30.7135 | 33.273 | 35.8325 | 38.3919 | 40.9514 | 43.5109 | 46.0703 | 48.6298 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892 | 51.1892

## SWIS renewable planting list
Assumed renewable connections
Based on public announcements and consultation with the PUO.
Assumed capacity factors based on historical data for existing projects. For new entrants, capacity factors are indicative and are assumed in consultation with the PUO.
Other renewables in excess of LRET may be built based on market outcomes.
Commissioning date | Project | Capacity (MW) | Load area | Technology | Capacity factor
Existing | ALINTA_WWF | 89.1 | North Country | Wind turbine | 0.42
Existing | ALBANY_WF1 | 21.6 | Albany | Wind turbine | 0.31
Existing | EDWFMAN_WF1 | 79.2 | North Country | Wind turbine | 0.35
Existing | INVESTEC_COLLGAR_WF1 | 206 | East Country | Wind turbine | 0.37
Existing | GRASMERE_WF1 | 13.8 | Albany | Wind turbine | 0.33
Existing | GREENOUGH_RIVER_PV1 | 10 | North Country | Fixed Plate PV | 0.25
Existing | MWF_MUMBIDA_WF1 | 55 | North Country | Wind turbine | 0.39
by 2022 | Byford Solar | 30 | Kwinana | Single axis tracking PV | 0.29
by 2022 | Greenough River 2 | 30 | North Country | Single axis tracking PV | 0.29
by 2022 | Emu Downs Solar Farm | 20 | North Country | Single axis tracking PV | 0.29
by 2022 | Northam Solar Project | 9.9 | East Country | Single axis tracking PV | 0.27
by 2022 | Badgingarra | 130 | North Country | Wind turbine | 0.44
by 2022 | Warradarge Stage 1 | 180 | North Country | Wind turbine | 0.44
by 2022 | Cunderdin Solar Farm | 100 | East Country | Single axis tracking PV | 0.28

## Thermal generator retirements
Announced and suggested capacity developments
Based on public announcements further retirements may be implemented based on simulation outcomes.
Option 1
Project | Capacity (MW) | Tech | Retirement schedule | Comments
SWCJV_WORSLEY_COGEN_COG1 | 116.4 | OCGT | from study start | Retired.
GERALDTON_GT1 | 20.8 | OCGT | from study start | Retired.
KWINANA_GT1 | 20.8 | OCGT | 2018-10-01 | https://www.synergy.net.au/About-us/News-and-announcements/Media-releases/Synergy-to-Reduce-Generation-Capacity-by-380-MW
MUJA_G1 (Muja A) | 55 | Black Coal | 2018-10-01
MUJA_G2 (Muja A) | 55 | Black Coal | 2018-10-01
MUJA_G3 (Muja B) | 55 | Black Coal | 2018-10-01
MUJA_G4 (Muja B) | 55 | Black Coal | 2018-10-01
MUNGARRA_GT1 | 37.2 | OCGT | 2018-10-01
MUNGARRA_GT2 | 37.2 | OCGT | 2018-10-01
MUNGARRA_GT3 | 38.2 | OCGT | 2018-10-01
WEST_KALGOORLIE_GT2 | 38.2 | Distillate | 2018-10-01
WEST_KALGOORLIE_GT3 | 24 | Distillate | 2018-10-01

## Energy forecasts
Operational energy forecasts for the WEM
Sources: | AEMO ESOO 2017, reduced by 246 to account for small generators not modelled. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
For extrapolated values to 2031-32, refer to the Appendix of the methodology report accompanying this workbook.
Targets shown are 'Operational, sent-out'
;Operational energy (GWh p.a. sent-out) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| High | 18463.9934 | 18766.4953 | 18977.1896 | 19198.9705 | 19493.1499 | 19817.0818 | 20177.875 | 20566.5359 | 21011.4201 | 21490.4055 | 22020.9477
| Expected | 18398.3784 | 18618.5294 | 18760.4849 | 18917.4788 | 19135.777 | 19356.3341 | 19588.8649 | 19830.9084 | 20106.4641 | 20414.4446 | 20749.5961
| Low | 18335.5178 | 18487.2085 | 18565.7591 | 18653.0331 | 18790.4234 | 18922.6784 | 19057.0004 | 19190.1181 | 19346.0557 | 19509.7018 | 19688.9367

## Peak demand forecasts
Operational peak demand forecasts for the WEM
Sources: | AEMO ESOO 2017, reduced by 28 to account for small generators not modelled. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
Note that the modelled operational peak demands modelled might differ to these numbers due to the explicit modelling of rooftop PV and storage behaviour, which depends on the reference year(s) used.
For extrapolated values to 2031-32 see the chart in the Appendix of the methodology report accompanying this workbook.
Targets shown are 'Operational, sent-out'
;Annual peak demand (MW) 10% POE |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| High | 4266.125 | 4364.0267 | 4462.2006 | 4569.1559 | 4688.0614 | 4801.5961 | 4930.9959 | 5070.7829 | 5219.9219 | 5379.0978
| Expected | 4140.716 | 4184.6154 | 4224.8907 | 4297.5432 | 4372.7058 | 4437.8866 | 4513.2926 | 4598.1876 | 4679.4409 | 4770.7019
| Low | 4076.1622 | 4097.6677 | 4124.8538 | 4163.7707 | 4198.5619 | 4229.3451 | 4279.1569 | 4316.7427 | 4360.3804 | 4418.9637

## Reserve capacity target
Reserve capacity target for the WEM
Sources: | AEMO ESOO 2017, reduced by 28 to account for small generators not modelled. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
Reserve Capacity Targets are based on the 10% POE peak demand forecasts taking into account reserve margins, intermittent loads and load following requirements
2017 High | AEMO High demand scenario
2017 Medium | AEMO Medium demand scenario
2017 Low | AEMO Low demand scenario
;Reserve capacity target (MW) |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| High | 4673.125 | 4771.0267 | 4869.2006 | 4976.1559 | 5095.0614 | 5208.5961 | 5337.9959 | 5477.7829 | 5626.9219 | 5787.9092
| Expected | 4547.716 | 4591.6154 | 4631.8907 | 4704.5432 | 4779.7058 | 4844.8866 | 4920.2926 | 5005.1876 | 5086.4409 | 5177.7019
| Low | 4483.1622 | 4504.6677 | 4531.8538 | 4570.7707 | 4605.5619 | 4636.3451 | 4686.1569 | 4723.7427 | 4767.3804 | 4825.9637

## Rooftop PV forecasts
Rooftop PV forecasts for the WEM
Sources: | Source: 2017 ESOO for the WEM. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
For extrapolated values to 2031-32 see the chart in the Appendix of the methodology report accompanying this workbook.
2017 Medium: | Expected rooftop PV uptake
2017 Low: | Low rooftop PV uptake
2017 High: | High rooftop PV uptake
;Capacity (MW) |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| 2017 AEMO ESOO (High) | 859 | 999 | 1147 | 1299 | 1450 | 1600 | 1750 | 1896 | 2039 | 2169
| 2017 AEMO ESOO (Expected) | 843 | 949 | 1059 | 1171 | 1283 | 1396 | 1509 | 1623 | 1736 | 1850
| 2017 AEMO ESOO (Low) | 818 | 896 | 980 | 1065 | 1150 | 1236 | 1323 | 1409 | 1494 | 1576
;Energy (GWh p.a. sent-out) |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| 2017 AEMO ESOO (High) | 1595.2661 | 1855.2629 | 2130.1166 | 2412.3989 | 2692.824 | 2971.392 | 3249.96 | 3521.0995 | 3786.6677 | 4028.0933
| 2017 AEMO ESOO (Expected) | 1565.5522 | 1762.4069 | 1966.6901 | 2174.6875 | 2382.685 | 2592.5395 | 2802.3941 | 3014.1058 | 3223.9603 | 3435.672
| 2017 AEMO ESOO (Low) | 1519.1242 | 1663.9795 | 1819.9776 | 1977.8328 | 2135.688 | 2295.4003 | 2456.9698 | 2616.6821 | 2774.5373 | 2926.8211
High
Expected
Low

## Battery storage forecasts
Behind-the-meter (domestic) storage uptake forecasts for the WEM
Sources: | Source: 2017 ESOO for the WEM. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
Large-scale storage could be installed in addition to the below forecast, if profitable.
As per AEMO's assumptions, assumes negligible contributions to peak demand from behind-the-meter storage.
For extrapolated values to 2031-32 see the chart in the Appendix of the methodology report accompanying this workbook.
2017 High: | High storage uptake
2017 Medium: | Medium storage uptake |  |  |  | Average size battery: | 10 | kWh
2017 Low: | Low storage uptake |  |  |  | Average size battery: | 5 | kW
;Capacity (MW) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| 2017 AEMO ESOO (High) | 16.3 | 44.1059 | 85.7059 | 135.3059 | 184.9059 | 234.5059 | 283.1059 | 331.7059 | 379.3059 | 425.9059 | 458.5059
| 2017 AEMO ESOO (Medium) | 16.4 | 40.7 | 70 | 105.8111 | 142.6222 | 178.4333 | 215.2444 | 251.0556 | 285.7389 | 319.4222 | 351.0833
| 2017 AEMO ESOO (Low) | 16.3 | 31.7882 | 53.2765 | 79.6824 | 103.6824 | 127.6824 | 151.6824 | 175.6824 | 199.6824 | 223.6824 | 247.6824
;Energy (MWh sent-out) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| 2017 AEMO ESOO (High) | 32.6 | 88.2118 | 171.4118 | 270.6118 | 369.8118 | 469.0118 | 566.2118 | 663.4118 | 758.6118 | 851.8118 | 917.0118
| 2017 AEMO ESOO (Medium) | 32.8 | 81.4 | 140 | 211.6222 | 285.2444 | 356.8667 | 430.4889 | 502.1111 | 571.4778 | 638.8444 | 702.1667
| 2017 AEMO ESOO (Low) | 32.6 | 63.5765 | 106.5529 | 159.3647 | 207.3647 | 255.3647 | 303.3647 | 351.3647 | 399.3647 | 447.3647 | 495.3647
;Peak demand reduction from battery storage (MW p.a. sent-out) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| 2017 AEMO ESOO (High) | 4.075 | 11.0265 | 21.4265 | 33.8265 | 46.2265 | 58.6265 | 70.7765 | 82.9265 | 94.8265 | 106.4765 | 114.6265
| 2017 AEMO ESOO (Medium) | 4 | 10 | 18 | 26 | 36 | 45 | 54 | 63 | 71 | 80 | 88
| 2017 AEMO ESOO (Low) | 3.725 | 7.225 | 12.225 | 18.725 | 24.725 | 30.725 | 36.725 | 42.725 | 48.725 | 54.725 | 60.725

## Electric vehicles
Electric vehicle uptake
Source: 2017 ESOO for the WEM. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
For extrapolated values to 2031-32 see the chart in the Appendix of the methodology report accompanying this workbook.
; Annual energy required by EVs (GWh) |  | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| High | 3.2 | 9.3 | 19.1 | 31.7 | 49 | 85.3 | 143.1 | 214.9 | 297.9 | 387.7 | 481.6
| Expected | 1.1 | 2.9 | 6.3 | 11.1 | 18 | 29 | 45.4 | 67.8 | 96.1 | 141 | 200.6
| Low | 0.5 | 1.1 | 2.4 | 4.2 | 6.4 | 10 | 15.7 | 24 | 34.9 | 48.1 | 63.1

## Fuel prices GSOO
Gas fuel costs for new contracts | [11 empty] | CPI Q2 2015 | 107.5
Sources: | AEMO GSOO Dec 2017: | Gas Statement of Opportunities - December 2017, AEMO. https://www.aemo.com.au/-/media/Files/Gas/National_Planning_and_Forecasting/WA_GSOO/2017/2017-WA-GSOO.pdf | [9 empty] | CPI Q2 2016 | 108.6
| Real June 2017 dollars | [10 empty] | CPI Q2 2017 | 110.7
| For extrapolated values to 2031-32 see the chart in the Appendix of the methodology report accompanying this workbook. | [10 empty] | CPI Q4 2017 | 112.1
;Gas prices ($/GJ) |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| GSOO (High) | 6.804 | 7.2878 | 8.1865 | 8.9074 | 9.4258 | 9.801 | 10.1072 | 10.3886 | 10.6503 | 10.7984
| GSOO (Base) | 5.3227 | 5.2486 | 5.3523 | 5.5301 | 5.6338 | 5.9547 | 6.7299 | 7.352 | 7.3767 | 7.5495
| GSOO (Low) | 5.2832 | 4.6166 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95
Direct from Gas Statement of Opportunities - December 2017, AEMO, in real December 2017 dollars
|  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
| GSOO (High) | 6.89 | 7.87 | 8.71 | 9.33 | 9.76 | 10.09 | 10.38 | 10.66 | 10.91 | 10.96
| GSOO (Base) | 5.39 | 5.24 | 5.6 | 5.6 | 5.81 | 6.25 | 7.38 | 7.51 | 7.43 | 7.86
| GSOO (Low) | 5.35 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4

## Fuel prices existing units
Fuel costs for new and existing generators including delivery
Sources: | AEMO GSOO Dec 2017: | Gas Statement of Opportunities - December 2017, AEMO. https://www.aemo.com.au/-/media/Files/Gas/National_Planning_and_Forecasting/WA_GSOO/2017/2017-WA-GSOO.pdf
| Jacobs IMO assumptions: | Jacobs for IMO, 2018/19 Margin Peak and Margin Off-peak Review, Final assumptions report - PUBLIC, 23 September 2017. https://www.erawa.com.au/cproot/18657/2/20180131_AEMO%2019%20Margin%20Peak%20Review%20V2_markup.PDF
Jacobs for IMO, 2016/17 Margin Peak and Margin Off-peak Review. Assumptions report - PUBLIC, 18 September 2015. https://www.aemo.com.au/media/docs/default-source/rules/other-wem-consultation-docs/assumptions-report--v1-3-public-cleanf6a0.pdf?sfvrsn=0
Assumptions: | Coal and liquid fuel prices kept constant (and as such alternative maximum market price also kept constant)
All prices on this sheet in real June 2017 dollars
|  | Margin Peak off-peak Review (IMO) fuel prices ($/GJ) by technology type. | [6 empty] | Margin Peak off-peak Review (IMO) distillate transport costs ($/GJ) by zone.
|  | 2016-17 |  |  | 2018-19 |  |  |  | 2016-17 |  | 2018-19
| Black Coal | 2.6053 |  |  | 2.6 |  |  | Goldfields | 1.5035 |  | 1.38
| Cogeneration | 2.9348 |  |  | 2.88 |  |  | Perth | 0.35 |  | 0.35
| Synergy contract gas | 3.4497 | [5 empty] | East Country | 1.5035 |  | 1.38
| New gas | 6.8891 |  |  | 5.91 |  |  | North Country | 1 |  | 1
| Distillate | 18.4843 |  |  | 16.23
Select GSOO gas price trajectory: | 2
|  |  |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
$/GJ
|  | 2016-17 |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
| Average gas spot price reported in the Jacobs report for 2016-17: | 4.6 | GSOO (Base) | 5.3227 | 5.2486 | 5.3523 | 5.5301 | 5.6338 | 5.9547 | 6.7299 | 7.352 | 7.3767 | 7.5495
|  | $/GJ |  | 2017-18: Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17.
Facility code | Fuel type | Starting price (2016-17) |  | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
ALCOA_WGP | Cogeneration | 4.0676 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
ALINTA_PNJ_U1 | Cogeneration | 4.0676 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
ALINTA_PNJ_U2 | Cogeneration | 4.0676 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
ALINTA_WGP_GT | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
ALINTA_WGP_U2 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
BW1_BLUEWATERS_G2 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
BW2_BLUEWATERS_G1 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
COCKBURN_CCG1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
COLLIE_G1 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
KEMERTON_GT11 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
KEMERTON_GT12 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
KWINANA_GT1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
KWINANA_GT2 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
KWINANA_GT3 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
MUJA_G1 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G2 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G3 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G4 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G5 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G6 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G7 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUJA_G8 | Black Coal | 2.6053 |  | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116 | -0.0053116
MUNGARRA_GT1 | New Gas | 7.713 |  | 0.65887 | 0.58481 | 0.6885 | 0.86625 | 0.96994 | 1.2909 | 2.0661 | 2.6882 | 2.7129 | 2.8857
MUNGARRA_GT2 | New Gas | 7.713 |  | 0.65887 | 0.58481 | 0.6885 | 0.86625 | 0.96994 | 1.2909 | 2.0661 | 2.6882 | 2.7129 | 2.8857
MUNGARRA_GT3 | New Gas | 7.713 |  | 0.65887 | 0.58481 | 0.6885 | 0.86625 | 0.96994 | 1.2909 | 2.0661 | 2.6882 | 2.7129 | 2.8857
NAMKKN_MERR_SG1 | Distillate | 19.9878 |  | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778
NEWGEN_KWINANA_CCG1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
NEWGEN_NEERABUP_GT1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PERTHENERGY_KWINANA_GT1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT1 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT10 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT11 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT2 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT3 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT4 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT5 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT7 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PINJAR_GT9 | New Gas | 8.0219 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PPP_KCP_EG1 | Cogeneration | 4.0676 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
PRK_AG | New Gas | 7.935 |  | 0.6368 | 0.56274 | 0.66642 | 0.84418 | 0.94787 | 1.2688 | 2.044 | 2.6661 | 2.6908 | 2.8636
STHRNCRS_EG | New Gas | 7.9459 |  | 0.6359 | 0.56184 | 0.66553 | 0.84328 | 0.94697 | 1.2679 | 2.0431 | 2.6652 | 2.6899 | 2.8627
TESLA_GERALDTON_G1 | Distillate | 19.4843 |  | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543
TESLA_KEMERTON_G1 | Distillate | 19.9878 |  | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778
TESLA_NORTHAM_G1 | Distillate | 19.9878 |  | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778
TESLA_PICTON_G1 | Distillate | 18.8343 |  | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543 | -2.2543
TIWEST_COG1 | Cogeneration | 4.0676 |  | 0.63994 | 0.56588 | 0.66957 | 0.84732 | 0.95101 | 1.2719 | 2.0471 | 2.6693 | 2.694 | 2.8668
WEST_KALGOORLIE_GT2 | Distillate | 19.9878 |  | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778
WEST_KALGOORLIE_GT3 | Distillate | 19.9878 |  | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778 | -2.3778
New generators (or post fuel contract)
New gas generator (Muja region) | New Gas | 4.6 |  | 0.72269 | 0.64862 | 0.75231 | 0.93006 | 1.0338 | 1.3547 | 2.1299 | 2.752 | 2.7767 | 2.9495
Transport cost ($/GJ) | Zone (Diesel) | Starting price (2016-17) |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2017-18: 2017-18; Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 2018-19
ALCOA_WGP |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
ALINTA_PNJ_U1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
ALINTA_PNJ_U2 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
ALINTA_WGP_GT |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
ALINTA_WGP_U2 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
BW1_BLUEWATERS_G2 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
BW2_BLUEWATERS_G1 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
COCKBURN_CCG1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
COLLIE_G1 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
KEMERTON_GT11 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
KEMERTON_GT12 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
KWINANA_GT1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
KWINANA_GT2 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
KWINANA_GT3 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
MUJA_G1 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G2 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G3 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G4 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G5 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G6 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G7 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUJA_G8 |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0
MUNGARRA_GT1 |  | 0.82381 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.76
MUNGARRA_GT2 |  | 0.82381 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.76
MUNGARRA_GT3 |  | 0.82381 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.76
NAMKKN_MERR_SG1 | East Country | 1.5035 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.38
NEWGEN_KWINANA_CCG1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
NEWGEN_NEERABUP_GT1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PERTHENERGY_KWINANA_GT1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT10 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT11 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT2 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT3 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT4 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT5 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT7 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PINJAR_GT9 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PPP_KCP_EG1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
PRK_AG | Goldfields | 1.0459 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.96
STHRNCRS_EG | Goldfields | 1.0568 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.97
TESLA_GERALDTON_G1 | North Country | 1 | bar: Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19
TESLA_KEMERTON_G1 | East Country | 1.5035 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.38
TESLA_NORTHAM_G1 | East Country | 1.5035 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.38
TESLA_PICTON_G1 | Perth | 0.35 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0.35
TIWEST_COG1 |  | 1.1327 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.05
WEST_KALGOORLIE_GT2 | Goldfields | 1.5035 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.38
WEST_KALGOORLIE_GT3 | Goldfields | 1.5035 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 1.38
New gas generator (Muja region) |  | 0 |  | Fuel price uplift assigned to each generator in each forecast year, relative to 2016-17. 2018-19: 0

## Capex
Capital costs for new technologies including connection costs
Real June 2016 AUD/kW
Source: 2016 NTNDP. http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/National-Transmission-Network-Development-Plan/NTNDP-database
Source: CSIRO/Jacobs for the AEMO National Electricity Forecasting Report (2016). https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/NEFR/2016/Projections-of-uptake-of-smallscale-systems.pdf
For adjusted wind and solar PV capital costs and storage cost extrapolation to 2031-32 see the charts in the Appendix of the methodology report accompanying this workbook.
Capex Real June 2016 AUD/kW nameplate
| Capital costs (for year of completion) (Real June 2016 $/kW nameplate) | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
| Black Coal - SC | 3216 | 3201 | 3186 | 3171 | 3155 | 3140 | 3125 | 3111 | 3096 | 3081 | 3066 | 3052 | 3037 | 3023 | 3008 | 2994
| Black Coal - SC - w CCS | 7054 | 7031 | 7009 | 6987 | 6964 | 6942 | 6695 | 6456 | 6227 | 6005 | 5792 | 5586 | 5388 | 5197 | 5175 | 5153
| CCGT | 1568 | 1568 | 1568 | 1568 | 1558 | 1549 | 1543 | 1537 | 1535 | 1532 | 1530 | 1528 | 1528 | 1528 | 1528 | 1526
| CCGT - w CCS | 3226 | 3222 | 3218 | 3214 | 3210 | 3206 | 2946 | 2707 | 2489 | 2288 | 2104 | 1936 | 1781 | 1639 | 1635 | 1630
| OCGT | 1107 | 1102 | 1097 | 1092 | 1086 | 1081 | 1076 | 1071 | 1066 | 1061 | 1057 | 1052 | 1047 | 1042 | 1037 | 1032
| Solar PV - Fixed | 1927 | 1868 | 1816 | 1760 | 1703 | 1681 | 1659 | 1641 | 1625 | 1487 | 1362 | 1248 | 1144 | 1049 | 1040 | 966
| Solar PV - SAT | 2273 | 2203 | 2140 | 2073 | 2007 | 1980 | 1954 | 1932 | 1914 | 1750 | 1600 | 1465 | 1341 | 1229 | 1217 | 1129
| CST central receiver - 6h storage | 7899 | 7586 | 7334 | 7136 | 6975 | 6447 | 5919 | 5390 | 5122 | 5013 | 4153 | 3931 | 3916 | 3903 | 3892 | 3882
| Wind | 2816 | 2728 | 2650 | 2567 | 2483 | 2449 | 2418 | 2390 | 2367 | 2162 | 1976 | 1806 | 1652 | 1511 | 1497 | 1387
Large-scale storage (2 hours) (Real June 2016 $/kW nameplate). Includes linear interpolation and extrapolation.
| CSIRO/Jacobs (Neutral scenario) | 880 | 800 | 740 | 680 | 636 | 590 | 560 | 530 | 516 | 500 | 476 | 450 | 426 | 400
| CSIRO/Jacobs (Weak scenario) | 990 | 900 | 840 | 780 | 720 | 660 | 635 | 610 | 585 | 560 | 555 | 550 | 500 | 450
| CSIRO/Jacobs (Strong scenario) | 750 | 680 | 635 | 590 | 550 | 510 | 485 | 460 | 440 | 420 | 400 | 380 | 365 | 350
;Capital costs (for year of completion) (Real June 2016 $/kW nameplate) | Capital costs (for year of completion) (Real June 2016 $/kW nameplate) | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32
_ | Black Coal | 3216 | 3201 | 3186 | 3171 | 3155 | 3140 | 3125 | 3111 | 3096 | 3081 | 3066 | 3052 | 3037 | 3023 | 3008 | 2994
_ | CCGT | 1568 | 1568 | 1568 | 1568 | 1558 | 1549 | 1543 | 1537 | 1535 | 1532 | 1530 | 1528 | 1528 | 1528 | 1528 | 1526
_ | OCGT | 1107 | 1102 | 1097 | 1092 | 1086 | 1081 | 1076 | 1071 | 1066 | 1061 | 1057 | 1052 | 1047 | 1042 | 1037 | 1032
_ | Solar PV - Fixed | 1927 | 1868 | 1816 | 1760 | 1703 | 1681 | 1659 | 1641 | 1625 | 1487 | 1362 | 1248 | 1144 | 1049 | 1040 | 966
_ | Solar PV - SAT | 2273 | 2203 | 2140 | 2073 | 2007 | 1980 | 1954 | 1932 | 1914 | 1750 | 1600 | 1465 | 1341 | 1229 | 1217 | 1129
_ | Wind | 2816 | 2728 | 2650 | 2567 | 2483 | 2449 | 2418 | 2390 | 2367 | 2162 | 1976 | 1806 | 1652 | 1511 | 1497 | 1387

## New entrant params
New entrant technology parameters
Source: 2016 NTNDP. http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/National-Transmission-Network-Development-Plan/NTNDP-database
Source: 2017 ESOO for the WEM. https://www.aemo.com.au/Electricity/Wholesale-Electricity-Market-WEM/Planning-and-forecasting/WEM-Electricity-Statement-of-Opportunities
Source: 2017 NEM ESOO. https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/NEM-Electricity-Statement-of-Opportunities
Source: IMO Planning Criterion Review. https://www.erawa.com.au/cproot/15250/2/Market%20Reform%20Presentation%20-%20Review%20of%20Planning%20Criterion.pdf
Source: Electricity and Gas Market Benefits and Costs of an Energy Efficiency Obligation Scheme. https://industry.gov.au/Energy/EnergyEfficiency/Documents/energy-efficiency/electricity-gas-market-benefits-costs-energy-efficiency-obligation-scheme.pdf
- also applied to existing units where unit-specific data is not available
Costs in real June 2016 AUD
Sources: | 2016 NTNDP | 2016 NTNDP | 2016 NTNDP | 2016 NTNDP | 2016 NTNDP | IMO Planning Criterion Review | 2017 NEM ESOO | IMO Planning Criterion Review | 2017 NEM ESOO | 2017 NEM ESOO | Electricity and Gas Market Benefits…
NTNDP technology | Auxiliaries (%) | FOM ($/MW) | VOM ($/MWh sent-out) | Economic life (years) | Emissions captured (%) | Full forced outage rate (%) | Mean time to repair - full (hours) | Partial forced outage rate (%) | Partial derating (%) | Mean time to repair - partial (hours) | Maintenance outage rate (days per year)
Black Coal - SC | 6.505% | 42073 | 3 | 30 | 0% | 1.72% | 55.03 | 9.88% | 26.17% | 26.62 | 3
Black Coal - SC - w CCS | 21.17% | 43359 | 10 | 30 | 90% | 1.72% | 55.03 | 9.88% | 26.17% | 26.62 | 3
CCGT / Cogeneration | 3% | 10000 | 7 | 30 | 0% | 3.02% | 14.05 | 7.84% | 29.88% | 71.64 | 2
CCGT - w CCS | 11.6% | 30941 | 12 | 30 | 80% | 3.02% | 14.05 | 7.84% | 29.88% | 71.64 | 2
OCGT - gas fuel | 1% | 4000 | 10 | 30 | 0% | 3.02% | 33.55 | 7.84% | 31.89% | 10.75 | 1
OCGT - liquid fuel | 1% | 4000 | 10 | 30 | 0% | 1.06% | 33.55 | 5.22% | 31.89% | 10.75 | 1
Solar PV - Fixed | 0% | 25000 | 0 | 25 | 0% | Included in modelled half-hourly availability profile.
Solar PV - SAT | 1% | 30000 | 0 | 25 | 0%
Solar PV - DAT | 0% | 40000 | 0 | 25 | 0%
CST central receiver - 6h storage | 0% | 65000 | 4 | 30 | 0%
Wind | 1% | 45000 | 0 | 25 | 0%
Large-scale storage (4 hours) | 0% | 0 | 0 | 15 | 0% | No data - assume 0%

## FORs
Generator outage rate data
IMO Planning Criterion Review. https://www.erawa.com.au/cproot/15250/2/Market%20Reform%20Presentation%20-%20Review%20of%20Planning%20Criterion.pdf
We propose to use the average outage rates from the above report.
Fuel type | Full forced outage rate (%) | [5 empty] | Planned forced outage rate (%)
| 2007 | 2008 | 2009 | 2010 | 2011 | Avg | 2007 | 2008 | 2009 | 2010 | 2011 | Avg
Coal | 1.4 | 2.1 | 1 | 2.1 | 2 | 1.72 | 8.9 | 8.3 | 8.3 | 12 | 11.9 | 9.88
Gas | 4 | 6.5 | 0.8 | 1 | 2.8 | 3.02 | 4.4 | 6.5 | 7.9 | 10.1 | 10.3 | 7.84
Gas/Liquid | 0.2 | 0.6 | 1.9 | 1.3 | 1.3 | 1.06 | 3.1 | 3.5 | 6.9 | 8.6 | 4 | 5.22

## MLFs
Generator marginal loss factors assumed in the forward-looking modelling
Table provided by the PUO for the constrained access modelling |  |  |  | Units modelled, with mapping
Code | Location | MU_refnode | ST_refnode | Unit_ID | Mapping to WP Code | ST_refnode MLF
WWWF | Walkaway Windfarm | 0.9519 | 0.9295 | ALBANY_WF1 | QALB | 0.9725 | * Note that Albany_WF1 is provided a DLF. This is the 2017-18 value referred to the MU Bus
TMBA | Mumbida Wind Farm | 0.9696 | 0.9472 | ALCOA_WGP | WWGP | 0.9577
WWGP | Wagerup | 0.9825 | 0.9577 | ALINTA_PNJ_U1 | TAPL | 0.9657
TWOJ | Worsley (Joint Venture) | 0.9821 | 0.9584 | ALINTA_PNJ_U2 | TAPL | 0.9657
TWOW | Worsley (Worsley) | 0.9866 | 0.963 | ALINTA_WGP_GT | TLWA | 0.9831
TAPL | Alcoa Pinjarra (Alinta) | 0.9898 | 0.9657 | ALINTA_WGP_U2 | TLWA | 0.9831
WCGW | Collgar Windfarm | 0.9923 | 0.9684 | ALINTA_WWF | WWWF | 0.9295
TAPA | Alcoa Pinjarra (Alcoa) | 0.9921 | 0.9687 | BW1_BLUEWATERS_G2 | TBLB | 0.9752
TMDP | Merredin Power Station (Nammarkin) | 0.9997 | 0.9694 | BW2_BLUEWATERS_G1 | TBLB | 0.9752
WCPS | Collie PWS | 0.9966 | 0.9713 | COCKBURN_CCG1 | WCCT | 1.0042
WWCL | Western Collieries | 0.9956 | 0.9718 | COLLIE_G1 | WCPS | 0.9713
WMPS | Muja PWS | 1 | 0.9738 | DSM 1 | N/A | 1
TBLB | Bluewaters | 0.9998 | 0.9752 | DSM 2 | N/A | 1
WKEM | Kemerton PWS | 1.0101 | 0.9788 | DSM 3 | N/A | 1
WMGA | Mungarra GTs | 1.0059 | 0.9795 | DSM 4 | N/A | 1
WBOD | Boddington | 1.0083 | 0.983 | DSM 5 | N/A | 1
TLWA | Lanwehr (Alinta) | 1.0129 | 0.9831 | DSM 6 | N/A | 1
WBGM | Boddington Gold Mine | 1.0093 | 0.9852 | EDWFMAN_WF1 | WEMD | 0.991
WMRR | Marriot Road | 1.0106 | 0.9862 | GRASMERE_WF1 | QAWF | 0.9725 | * Note that Grasmere_WF1 is provided a DLF. This is the 2017-18 value referred to the MU Bus, based on Albany_WF1
WBUH | Bunbury Harbour | 1.0138 | 0.9882 | GREENOUGH_RIVER_PV1 | TMGS | 0.9924
WBSI | Marriott Road Barrack Silicon Smelter | 1.0126 | 0.9883 | INVESTEC_COLLGAR_WF1 | WCGW | 0.9684
WBDP | Binningup Desalination Plant | 1.0127 | 0.9883 | KEMERTON_GT11 | WKEM | 0.9788
WPIC | Picton 66kv | 1.0136 | 0.9885 | KEMERTON_GT12 | WKEM | 0.9788
TOLA | Oakley (Alinta) | 1.0146 | 0.9897 | KWINANA_GT1 | WKPS | 0.998
WBTN | Bridgetown | 1.0145 | 0.9899 | KWINANA_GT2 | WKPS | 0.998
WEMD | Emu Downs | 1.0148 | 0.991 | KWINANA_GT3 | WKPS | 0.998
WPNJ | Pinjarra | 1.0167 | 0.9911 | MUJA_G1 | WMPS | 0.9738
TMGS | Greenough River Solar Farm (Mungarra) | 1.0187 | 0.9924 | MUJA_G2 | WMPS | 0.9738
WMJP | Manjimup | 1.0202 | 0.9945 | MUJA_G3 | WMPS | 0.9738
WKND | Kwinana Donaldson Road (Western Energy) | 1.0267 | 0.9957 | MUJA_G4 | WMPS | 0.9738
WCOE | Collie | 1.0226 | 0.997 | MUJA_G5 | WMPS | 0.9738
WHIS | Hismelt | 1.0219 | 0.9978 | MUJA_G6 | WMPS | 0.9738
WKPS | Kwinana PWS | 1.0236 | 0.998 | MUJA_G7 | WMPS | 0.9738
WNGK | NewGen Kwinana | 1.0231 | 0.9983 | MUJA_G8 | WMPS | 0.9738
WPLD | Parklands | 1.0248 | 0.9987 | MUNGARRA_GT1 | WMGA | 0.9795
WMSS | Meadow Springs | 1.0264 | 1 | MUNGARRA_GT2 | WMGA | 0.9795
WKMK | Kerr McGee Kwinana | 1.0245 | 1.0001 | MUNGARRA_GT3 | WMGA | 0.9795
WMHA | Mandurah | 1.0268 | 1.0007 | MWF_MUMBIDA_WF1 | TMBA | 0.9472
WGNI | Glen Iris | 1.0281 | 1.0007 | NAMKKN_MERR_SG1 | TMDP | 0.9694
WDUR | Durlacher | 1.0265 | 1.0005 | NEWGEN_KWINANA_CCG1 | WNGK | 0.9983
WGTN | Geraldton | 1.0265 | 1.0009 | NEWGEN_NEERABUP_GT1 | WGNN | 1.0066
TMSK | Mason Road (KPP) | 1.0261 | 1.0011 | PERTHENERGY_KWINANA_GT1 | WKND | 0.9957
WCBP | Mason Road CSBP | 1.0269 | 1.0011 | PINJAR_GT1 | WPJR | 1.0055
WMSR | Mason Road | 1.026 | 1.0015 | PINJAR_GT10 | WPJR | 1.0055
WAKW | Kwinana Alcoa | 1.0265 | 1.0015 | PINJAR_GT11 | WPJR | 1.0055
WKDP | Kwinana Desalination Plant | 1.0261 | 1.0016 | PINJAR_GT2 | WPJR | 1.0055
WRAN | Rangeway | 1.0275 | 1.0017 | PINJAR_GT3 | WPJR | 1.0055
WCPN | Chapman | 1.0286 | 1.0022 | PINJAR_GT4 | WPJR | 1.0055
WKOJ | Kojonup | 1.0284 | 1.0026 | PINJAR_GT5 | WPJR | 1.0055
WBHK | Broken Hill Kwinana | 1.028 | 1.0033 | PINJAR_GT7 | WPJR | 1.0055
WBNP | Beenup | 1.0283 | 1.0033 | PINJAR_GT9 | WPJR | 1.0055
WWMG | Western Mining | 1.0283 | 1.0033 | PPP_KCP_EG1 | TMSK | 1.0011
WAFM | Australian Fused Materials | 1.0282 | 1.0037 | PRK_AG | WPKS | 1.1196
WBPM | British Petroleum | 1.0287 | 1.0037 | STHRNCRS_EG | TBLS | 1.1502
WWLN | Willetton | 1.0297 | 1.0037 | TESLA_GERALDTON_G1 | QTCG | 0.97935 | * Note that Tesla units are provided a DLF. This is the 2017-18 value referred to the MU Bus
WMUR | Murdoch | 1.0298 | 1.0037 | TESLA_KEMERTON_G1 | QTES | 1.0223 | * Note that Tesla units are provided a DLF. This is the 2017-18 value referred to the MU Bus
WWSD | Westralian Sands | 1.0298 | 1.0037 | TESLA_NORTHAM_G1 | QTCN | 0.93091 | * Note that Tesla units are provided a DLF. This is the 2017-18 value referred to the MU Bus
WCCL | Cockburn Cement Ltd | 1.0288 | 1.0041 | TESLA_PICTON_G1 | QTES | 0.97943 | * Note that Tesla units are provided a DLF. This is the 2017-18 value referred to the MU Bus
WSNR | Southern River | 1.0304 | 1.0041 | TIWEST_COG1 | WKMK | 1.0001
WCCT | Cockburn Cement | 1.0303 | 1.0042 | WEST_KALGOORLIE_GT2 | TWKG | 1.1259
WMDN | Maddington | 1.0307 | 1.0044 | WEST_KALGOORLIE_GT3 | TWKG | 1.1259
WBEC | Beckenham | 1.0327 | 1.0066 | Byford Solar | WBYF | 1.007
WCVE | Canning Vale | 1.0305 | 1.0046 | Greenough River 2 | TMGS | 0.9924
WRTN | Riverton | 1.031 | 1.0047 | Emu Downs Solar Farm | WEMD | 0.991
WMED | Medina | 1.0309 | 1.0048 | Northam Solar Project | WNOR | 1.0314
WGNL | Gosnells | 1.0313 | 1.0048 | Badgingarra | WEMD | 0.991
WROH | Rockingham | 1.0314 | 1.0051 | Warradarge Stage 1 | WTST | 0.96 | * Based on estimated generation-weighted MLF outcomes
WPJR | Pinjar | 1.0322 | 1.0055 | Cunderdin Solar Farm | WCUN | 1.0568
WWAI | Waikiki | 1.032 | 1.0057 | Manjimup | WMJP | 0.9945
WWEL | Welshpool | 1.0321 | 1.0057 | Solar PV FFP - Bunbury | TWOJ | 0.9584
WKDL | Kewdale | 1.032 | 1.0059 | Solar PV FFP - East Country | WCGW | 0.9684
WTLN | Tomlinson Street | 1.03 | 1.0063 | Solar PV FFP - Eastern Goldfields | TWKG | 1.1259
WRVE | Rivervale | 1.0327 | 1.0063 | Solar PV FFP - Kwinana | WKPS | 0.998
WVPA | Victoria Park | 1.0352 | 1.009 | Solar PV FFP - Muja | WMPS | 0.9738
WBEL | Belmont | 1.0328 | 1.0064 | Solar PV FFP - Neerabup | WGNN | 1.0066
WTTS | Tate Street | 1.033 | 1.0066 | Solar PV FFP - North Country | TMGS | 0.9924
WGNN | Newgen Neerabup | 1.0374 | 1.0066 | Solar PV SAT - Bunbury | TWOJ | 0.9584
WBYF | Byford | 1.0338 | 1.007 | Solar PV SAT - East Country | WCGW | 0.9684
WBIB | Bibra Lake | 1.0342 | 1.0076 | Solar PV SAT - Eastern Goldfields | TWKG | 1.1259
WENB | Eneabba | 1.0336 | 1.0081 | Solar PV SAT - Kwinana | WKPS | 0.998
WKMC | Cataby Kerr McGee | 1.0349 | 1.0088 | Solar PV SAT - Muja | WMPS | 0.9738
WCAP | Capel | 1.0348 | 1.0093 | Solar PV SAT - Neerabup | WGNN | 1.0066
WBTY | Bentley | 1.0353 | 1.0095 | Solar PV SAT - North Country | WTST | 0.96 | * Based on estimated generation-weighted MLF outcomes
WHZM | Hazelmere | 1.0355 | 1.0097 | SWIS Biomass South | WMJP | 0.9945
WMJX | Midland Junction | 1.0368 | 1.0101 | Wind - Bunbury | TWOJ | 0.9584
WRGN | Regans | 1.0363 | 1.0107 | Wind - East Country | WCGW | 0.9684
WKMM | Muchea Kerr McGee | 1.0362 | 1.0114 | Wind - Eastern Goldfields | TWKG | 1.1259
WMUC | Muchea | 1.0378 | 1.0116 | Wind - Kwinana | WKPS | 0.998
WMLG | Malaga | 1.0379 | 1.0116 | Wind - Muja | WMPS | 0.9738
WAMT | Amherst | 1.0381 | 1.0116 | Wind - Neerabup | WGNN | 1.0066
WKDN | Kondinin | 1.0375 | 1.0117 | Wind - North Country | WTST | 0.96 | * Based on estimated generation-weighted MLF outcomes
WNOW | Nowgerup | 1.037 | 1.0119 | SWIS Bunbury CCGT 1 | TWOJ | 0.9584
WYCP | Yanchep | 1.0382 | 1.0119 | SWIS Bunbury CCGT 2 | TWOJ | 0.9584
WWNO | Wanneroo | 1.0385 | 1.012 | SWIS Bunbury OCGT 1 | TWOJ | 0.9584
WTSG | Three Springs | 1.0382 | 1.0122 | SWIS Bunbury OCGT 2 | TWOJ | 0.9584
WCLN | Clarence Street | 1.0389 | 1.0122 | SWIS East Country CCGT 1 | WCGW | 0.9684
WCOL | Collier | 1.039 | 1.0125 | SWIS East Country CCGT 2 | WCGW | 0.9684
WHBK | Henley Brook | 1.0401 | 1.013 | SWIS East Country OCGT 1 | WCGW | 0.9684
WNFL | North Fremantle | 1.0384 | 1.0131 | SWIS East Country OCGT 2 | WCGW | 0.9684
WEDD | Edmund Street | 1.0398 | 1.0131 | SWIS Eastern Goldfields CCGT 1 | TWKG | 1.1259
WCKN | Clarkson | 1.0413 | 1.0134 | SWIS Eastern Goldfields CCGT 2 | TWKG | 1.1259
WARK | Arkana | 1.04 | 1.0135 | SWIS Eastern Goldfields OCGT 1 | TWKG | 1.1259
WMDY | Munday | 1.0397 | 1.0137 | SWIS Eastern Goldfields OCGT 2 | TWKG | 1.1259
WBCH | Beechboro | 1.0404 | 1.0137 | SWIS Kwinana CCGT 1 | WKPS | 0.998
WFFD | Forrestfield | 1.0405 | 1.014 | SWIS Kwinana CCGT 2 | WKPS | 0.998
WJDP | Joondalup | 1.041 | 1.0143 | SWIS Kwinana OCGT 1 | WKPS | 0.998
WCTE | Cottesloe | 1.0414 | 1.0146 | SWIS Kwinana OCGT 2 | WKPS | 0.998
WDTN | Darlington | 1.0412 | 1.0147 | SWIS Muja CCGT 1 | WMPS | 0.9738
WAPM | Australian Paper Mills | 1.0411 | 1.0149 | SWIS Muja CCGT 2 | WMPS | 0.9738
WBCT | Balcatta | 1.0418 | 1.015 | SWIS Muja OCGT 1 | WMPS | 0.9738
WHFS | Hadfields | 1.0418 | 1.015 | SWIS Muja OCGT 2 | WMPS | 0.9738
WMOY | Morley | 1.042 | 1.0152 | SWIS Neerabup CCGT 1 | WGNN | 1.0066
WMIL | Milligan Street | 1.042 | 1.0153 | SWIS Neerabup CCGT 2 | WGNN | 1.0066
WYKE | Yokine | 1.0421 | 1.0153 | SWIS Neerabup OCGT 1 | WGNN | 1.0066
WOPK | Osborne Park | 1.0421 | 1.0155 | SWIS Neerabup OCGT 2 | WGNN | 1.0066
WKDA | Kalamunda | 1.0423 | 1.0155 | SWIS North Country CCGT 1 | WTST | 1 | * Based on estimated generation-weighted MLF outcomes
WJTE | Joel Terrace | 1.0422 | 1.0156 | SWIS North Country CCGT 2 | WTST | 1 | * Based on estimated generation-weighted MLF outcomes
WMUL | Mullaloo | 1.0423 | 1.0159 | SWIS North Country OCGT 1 | WTST | 1 | * Based on estimated generation-weighted MLF outcomes
WWGA | Wangara | 1.0425 | 1.016 | SWIS North Country OCGT 2 | WTST | 1 | * Based on estimated generation-weighted MLF outcomes
WLDE | Landsdale | 1.0429 | 1.0161
WSUM | Summer St | 1.0431 | 1.0161
WCKT | Cook Street | 1.043 | 1.0163
WHAY | Hay Street | 1.043 | 1.0163
WNBH | North Beach | 1.0431 | 1.0163
WNGN | Narrogin | 1.0427 | 1.0165
WNPH | North Perth | 1.0433 | 1.0165
WEDG | Edgewater | 1.0458 | 1.0167
WPBY | Padbury | 1.0437 | 1.0169
WSFT | South Fremantle 66kV | 1.0246 | 0.9987
WOCN | O'Connor | 1.0438 | 1.0171
WSRD | Sutherland | 1.0452 | 1.0174
TKRA | Karara Three Springs | 1.0432 | 1.0181
WWNT | Wellington Street | 1.046 | 1.0181
WTST | Three Springs Terminal | 1.0499 | 1.0181
WMAG | Manning Street | 1.049 | 1.0184
WSPA | Shenton Park | 1.0452 | 1.0186
WFRT | Forrest Ave | 1.0453 | 1.0187
WMYR | Myaree | 1.0458 | 1.0187
WBSN | Busselton | 1.0458 | 1.0194
WSVY | Sawyers Valley | 1.0458 | 1.0197
WUNI | University | 1.0456 | 1.02
WNED | Nedlands | 1.0471 | 1.0201
WMCR | Medical Centre | 1.0478 | 1.0207
WMWR | Mundaring Weir | 1.0479 | 1.0207
WWDN | Wembley Downs | 1.0479 | 1.0211
WHEP | Herdsman Parade | 1.0483 | 1.0215
WMOR | Moora | 1.0488 | 1.0222
WCLP | Coolup | 1.0484 | 1.0227
WWAG | Wagin | 1.0503 | 1.0242
WMER | Merredin 66kV | 1.0508 | 1.0245
WKAT | Katanning | 1.0521 | 1.0258
WMBR | Mt Barker | 1.0575 | 1.031
WNOR | Northam | 1.0582 | 1.0314
WBDE | Baandee (WC) | 1.0578 | 1.0324
WWUN | Wundowie | 1.0625 | 1.0357
WGGV | Golden Grove | 1.0629 | 1.0375
WKEL | Kellerberrin | 1.0706 | 1.0436
WALB | Albany | 1.0711 | 1.0439
WBNY | Bounty | 1.071 | 1.0455
WYLN | Yilgarn | 1.0753 | 1.0491
WCUN | Cunderdin | 1.0837 | 1.0568
WMRV | Margaret River | 1.0982 | 1.0708
WCAR | Carrabin | 1.1042 | 1.0776
WYER | Yerbillon | 1.108 | 1.0814
WBLD | Boulder | 1.1434 | 1.1158
WWKT | West Kalgoorlie | 1.1446 | 1.1166
WPKS | Parkeston | 1.1468 | 1.1196
WPCY | Piccadilly | 1.1528 | 1.1238
TWKG | West Kalgoorlie GTs | 1.1557 | 1.1259
WBKF | Black Flag | 1.1619 | 1.1339
TBLS | Boulder (SCE) | 1.1795 | 1.1502