## Legend
Legend
Blue cells - Actioned and closed
Pink cells - Propose to progress as separate issue
Green cells - For WG discussion on 2 July
Purple cells - Grandfather/transitional arrangement considerations - for WG discussion on 2 July
Grey - Issue Lead to progress further with sub-working group

## Comments and Response
Issue | Submission | Clause | Comment/Feedback | ISO Comments | Horizon Power Comments | BHP Comments | EPWA response
Issue 4/I2025.01 Issue Lead: David (HP) / Peter (ISO) | HP | Clause 2.2.2(c)(1) | Recommendation: Suggest: “An implementation of a specific voltage control operating target…. made under this subclause…..” (The voltage standards are not being changed - this is an operational setting) | No change | Agreed |  | Change not adopted. Suggested wording sufficiently clear.
|  | Figure 2.1 | Recommendation: This requires further definition. i.e. % of what? This is a percentage of ‘nominal’ voltage - so must define nominal for LV = 230V 1phase or 400V 3phase. E.g.. 10% overvoltage level is 440V….. Without defining the nominal, the overvoltage level is open to interpretation (eg some might incorrectly determine the 3ph overvoltage level at 100sec to be 440x1.1=484V which would be incorrect! Need to define the nominal voltages at LV (the higher voltages are defined elsewhere) and specify Percentage (of Nominal) Overvoltage envelope or issue explanatory note. Possibly add a clarifying curve similar to that added below | Further information required – prior to public consultation | Agreed |  | Added note to Figure 2.1 as suggested.
| BHP | Clause 2.2.2(a) | Clarification: has there been any analysis to check if there is an impact on residential PV (e.g. impacting disconnection settings), or existing loads that may be impacted by the change? | Question for EPWA. (HP have also provided an answer here). | Yes - this is not expected to have a material impact on residential PV with Australia Region C settings. The new voltage range is consistent with legislation which is now in effect. No change required. |  | Response to request for clarifcation via issue lead: "Yes - this is not expected to have a material impact on residential PV with Australia Region C settings. The new voltage range is consistent with legislation which is now in effect. No change required."
|  | Clause 2.2.2(c)(1) | Recommendation: We believe the defined terms in the PNR are “Inside the Technical Envelope” and “Outside the Technical Envelope”. Suggest re-wording clause around those defined terms rather than using the undefined “technical envelope” | Question for EPWA. | Agreed |  | Amended text to 'inside the technical envelope'.
|  | Clause 3.4.2(c)(2) | Recommendation: To avoid confusion, rather than using the range of voltages here suggest using the nominal voltage 230V and 400V (as the allowable ranges for these nominal voltages are now captured in clause 2.2.2(a) | Further information required – prior to public consultation | Agreed |  | Amended, with ISO suggested phrasing.
| ISO | Clause 3.4.2(c)(2) | Recommendation: Connection points should be characterised as their nominal voltage. E.g. we would not say a “297-363kV connection”, we would say “330kV connection” The acceptable range of voltages for the network is defined under 2.2.2, it does not need to be repeated here. Suggested phrasing: 1, 2 or 3 phase plus neutral, 230V or 400V | Further information required – prior to public consultation | Agreed ISO - Agree but seems like further consultation is needed to figure out the exact wording unless EPWA are happy to propose their own. |  | Amended, as suggested.
| APA | Clause 2.2.2(c)(1) | For clarity, rather than “this subclause” refer to “2.2.2(c)” directly. | Common sense. Implement change as written. | Agreed |  | Change not adopted. Suggested wording sufficiently clear.
| Confidential Submission | Clauses 2.2.10 + Figure 2.1 | Clarification: The draft introduces a single temporary over-voltage envelope (percentage overvoltage vs time). Previous versions applied separate distribution and transmission envelopes. The submmision requests confirmation about whether Figure 2.1 applies to both transmission and distribution. If the intent differs, retain separate envelopes or include an explanatory note. | Include clarification in the notes released with the new HTR but not in the HTR itself. | Clarify - add a note to the figure that this applies to both transmission and distribution. ISO - I don't think any change is necessary. The distinction is only relevant for somebody who has been reading the old rules. |  | The same envelope applied to both transmission and distribution. An explanatory note is not necessary as this is only confused by comparison to earlier versions.
Issue 8 Issue Lead: Peter (ISO) | HP | Clause 3.3.4.4(f)(1)© | Clarification: Can you please share with Horizon Power the basis of 2 seconds? It will be likely sufficient. Worth checking in future studies. | No change |  |  | Open question for Issue Lead. No change requested.
| BHP | Issue 8 | Clarification: There are a number of changes that have been proposed to generator performance standards, but no discussion as to whether these are intended to be retrospectively applied to existing generating facilities. Typically, compliance with generator performance standards is against the relevant standards that were applicable for the connection (or upgrade) at the time of access. Can the position on retrospective application please be clarified. | Decision point for EPWA: take existing drafting to public consultation; or revise drafting; or discuss further prior to public consultation. |  |  | WG query: Are grandfathering or transition arrangements required?
|  | Issue 8 | Recommendation: The term “storage works” has been added to a number of clauses, however the defined term in the HTR is “storage facility”. Suggest aligning to avoid confusion | Drafting choice for EPWA. |  |  | "Storage works" is the defined term used in the PNR and in legislation. Storage Facilties is incorrectly italicised in HTR clauses 3.7(a) and (b), because it isn't a defined term (facilities is, storage isn't). The use of the term Storage Facilities in clauses 3.7(a) and (b) has now been amended to Storage Works to align it with the PNR, legislation and the Amending Rules proposed under Issue 8.
|  | Clause 3.3.4.4(f) | Clarification: Assuming a battery is treated as a dispatchable generating unit for the purposes of this clause, batteries will have some limitations in meeting this from time to time (as depends on available charge). As written, this tends to place a requirement on batteries to maintain a specific level of available charge in order to be able to meet this frequency response requirement all the time – this is likely to have unintended design/cost/operation consequences. Alternatively, the clause could be adjusted to allow batteries to provide the required response based on available energy | I believe this suggestion takes us beyond the scope of the working groups intention- which I understood to be providing clarity for the application of section 3.7 in the absence of more detailed changes. I suggest that this could be advanced in parallel with public consultation to create a staged approach to HTR changes. Otherwise, further information is required prior to public consultation |  |  | Progress as separate issue.
| ISO | Clause 3.7(b)(2) | Recommendation: Italicise "consumer equipment" as a defined term | Amend as suggested |  |  | Amended.
| APA | Issue 8 | Recommendation: To deal with factors such as state of charge (SoC) and operating modes, which can limit the ability of units to respond, we recommend a clause at the start of the section (rather than adjusting individual clause as occurs in the WEM). This new clause can make it clear performance is considered alongside changed power system conditions and energy source availability. This would then equally be applied to all types of generators and BESS. | This is a good suggestion but I believe this would take us beyond the scope of the working groups intention- which I believe was to provide clarity for the application of section 3.7 in the absence of more detailed changes. I suggest that this could be advanced in parallel with public consultation to create a staged approach to HTR changes. Otherwise, further information is required prior to public consultation |  |  | Progress as separate issue.
|  |  | Recommendation: The drafting has not yet contemplated grid‑forming or grid‑following requirements (noting this is a future sub working group topic). APA considers these essential to facilitate a range of BESS technology. We request clauses being discussed in the working group be brought forward into this package of changes to the extent possible. Given the maturity of drafting that applies in the WEM, it make be possible to package these with the current Draft Amending Rules. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.3(b) | Recommendation: This clause requires amendment so it is tailored to BESS. BESS response is dependent on its state of charge (SoC) and its operating mode at the time of the event (i.e. charging or discharging). It would be better to state the requirement as being “subject to energy source availability” to avoid ambiguity. Proposed drafting [edits underlined in green]: A generating unit and a power station in which the generating unit is located must be capable of continuous uninterrupted operation within the power system frequency envelope specified in Figure 3.4, subject to energy source availability. Operation for a period of at least 20 seconds is required each time the frequency is below 47.5 Hz. Operation for a period of at least 6 seconds is required each time the frequency is above 52 Hz. Below 47 Hz and above 52.5 Hz, instantaneous disconnection of generating units is permitted. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.3(c) | Recommendation: Suggest reviewing use of “unit” versus “system” in this and include references to “energy source availability” as appropriate. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.3(d) | Clarification: Drafting is unclear if it’s a rate of change or maintaining a change indefinitely (open to interpretation depending on emphasis). It could be made clearer the RoCoF is up to 4 Hz per second, with reference to energy source availability. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.3(g) | Recommendation: This clause requires amendment so it is tailored to BESS. BESS usually have active power controller to regulate active power and reactive power, but the actual response post fault is dependent on its state of charge (SoC) and its operating mode at the time of the event (i.e. charging or discharging). It would be better to state the requirement as being “subject to energy source availability” to avoid ambiguity. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.3(h) | Recommendation: Clause 3.3.3.3(h)(2)(A) refers to variation in the primary source of energy, while other clauses in the section omit references to energy source availability. Consider updates across the section. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.3.4 | Recommendation: Similar to other comments, actual BESS response still limited by available energy and headroom. For a BESS, performance is also temperature dependent. If the battery temperature rises above its recommended operating range during rapid response, the BESS may derate or limit output (power and/or duration) to protect the cells and comply with the battery management system (BMS) limits. Consider update to clause to recognise limitation and/or use a general clause at the start of the section. | As above. |  |  | Progress as separate issue.
|  | Clause 3.3.4.4(c) | Recommendation: Use of the term “generator” needs clarification in this context. Should this be “controller”? | As above |  |  | Progress as separate issue.
|  | Clause 3.3.4.4(f) | Recommendation: Support refining this clause to be technology dependent. 2 seconds for non-synchronous generating units will be achievable for BESS under most conditions but likely too fast for other types of technology. Recommend the working group discuss having different requirements for types of generation (wind, solar, BESS) rather grouping all non-synchronous connections. This may be more efficient than connections seeking exemptions from the clause. | As above |  |  | Progress as separate issue.
|  | Clause 5.2.3(e) | Recommendation: Controller obligations in 5.2.3 link to obligations in clause 3.3.4.4. Given the proposed changes to frequency response times (i.e., 2 seconds for inverter technology), suggest this clause may require clarification or update. | Further information required – prior to public consultation |  |  | Open question for Issue Lead
| Confidential Submission | Clauses 3.3.4.4(f)(1)(A)–(C) and 3.3.4.4(f)(2) | Recommendation: This issue updates frequency control “rate of response” by adding a specific response time for non-synchronous generating units and retaining separate thermal/hydro timings. The submission notes that hydro generating units are unlikely to connect in the Pilbara; if hydro becomes relevant, the HTR can be updated on merit at that time. The submission requests ISO confirm hydro provisions are retained as generic drafting only (or make them conditional where hydro is proposed/connected) and clarify applicability/compliance expectations for the new non-synchronous requirement. | No change |  |  | Open question for Issue Lead. No change requested.
| Woodside | Issue 8 | If a base load renewable energy power station is to be developed at Maitland, the rule amendments will add substantial additional cost in the context of requirements for generating units including batteries and inverters. | No change |  |  | No change requested.
Issue 10 & 11 Issue Lead: Njabulo (BHP) | BHP | Clause 2.2.8 | Recommendation: The wording in this section could be simplified a little and would be easier to read with a table, e.g. below (note also that the defined term will need updating either way): Refer to edited definition of small disurtubance rotor angle stability and amended clause 2.2.8 in provided comments. |  |  | Agree. | Change reflected.
|  | Clause 3.3.1(d) | Clarification: What does EEA stand for in this context? Should this instead say “all generating units”? |  |  | EEA is used in HTR and not defined. Please investigate and include acronym description or re-phrase prior to finalising drafting | Amended as suggested.
|  | Clause 3.3.1(d) | Recommendation: Needs to be revised to align with proposed adjustments to clause 2.2.8. Suggest “reduced transient and oscillatory stability” |  |  | Agree. | Amended as requested.
|  | Clause 3.3.1(e)(2) - (3) | Recommendation: Worth noting that there is a dependency/relationship here the quantity of ESS procured by the ISO, and limiting the maximum size of the generating unit based on current ESS levels may not be optimal overall for the NWIS. Suggest revising the clause to allow for coordination with the ISO to make an assessment on whether the required levels of ESS can be procured and whether an increase in ESS is reasonable against the overall benefit of introducing the larger sized generating unit |  |  | I consider this a new issue that requires ISO to assess and accept this comment. Continue drafting and address as a separate new issue | Progress as separate issue.
|  | Clause 3.3.1(h) | Recommendation: Similar anti-islanding requirements may be needed in certain circumstances for transmission connected generating systems as well |  |  | Continue drafting and address as a separate new issue | Progress as separate issue.
|  | Clause 3.3.3.3(f) | Clarification: Without placing an obligation (as this would be difficult to measure compliance against), is it worth adding a note that there is still an expectation that reactive power equipment that is not a generating unit in a facility that is still connected following the disconnection of a generating unit, continues to provide reactive power support |  |  | Continue drafting and address as a separate new issue, however, suggestion sounds reasonable | Progress as separate issue.
| ISO | Clause 3.3.1(i) | Recommendation: Replace "dampening" with "damping" |  |  | Agree | Amended as requested.
| APA | Issue 10 and 11 | APA requests discussion on a damping method at an upcoming working group meeting. Happy to facilitate this discussion as needed. |  |  | Agree - please give APA opportunity to raise their views | Open question for Issue Lead.
|  | Clause 3.3.1(i) | Recommendation: Current drafting should be complemented by other clauses that hold performance standard constant of rate generator at the time of connection (or major modification). The amendment [when read alone] places an uncontrollable obligation on generating systems to ensure their connection to the power system does not degrade power system dampening as the affect at their connection can change as the system around them alters. This is particularly relevant for inverter-based generating units, whose damping performance can vary with network conditions. It would be preferable to define the applicable Short Circuit Ratio (SCR) at the time of connection (or major modification) as the basis for assessing damping performance. This can then be readily verified during compliance testing. Proposed drafting [edits underlined in green]: All generating systems must ensure that their connection to the power system does not degrade power system dampening relative to the thresholds established in clause 2.2.8 at the time of connection or major modification. |  |  | I suggest to consider this comment as part of the discussion offedered bt APA in comment above | Progress as separate issue.
Issue 13 Issue Lead: Neil (ISO) | HP | Clause 4.2.2.A(c) | Recommendation: Current drafting may cause confusion/ambiguity and suggest rewording the clauses as follows: (c) The ISO may issue an unconditional interim approval to generate only where the ISO, together with any relevant NSPs, is satisfied that the generating unit or generating system has shown no evidence of noncompliance with the applicable harmonised technical rule requirements based on observed performance, and that no risks to power system security or reliability have been identified. | Decision point for EPWA: take existing drafting to public consultation or revise drafting or discuss further prior to public consultation. |  |  | Amended as requested.
| BHP | Clause 1.5 | Clarification: Is the approval to generate notification issued by the ISO to a generator? (as opposed to the NSP as written) | No change |  |  | Amended to 'controller of generating unit or generating system', in line with request. Issue lead/WG to advise if this needs to apply to storage works as well? And if so, whether revised drafting in 4.2.2A captures this or if an alternative approach is recommended?
|  | Clause 1.5 | Clarification: Is the interim approval to generate notification issued by the ISO to a generator? (as opposed to the NSP as written) | No change |  |  | As above.
|  | Clause 1.5 | Recommendation: The generator monitoring plan definition refers to clause 4.1.3(c) however this section is quite light currently and does not cover any of the process related items associated with submitting/approving/revising a GMP. Suggest enhancing clause 4.1.3(c) to cater for this, and perhaps referencing an ISO procedure to cover things like the process for submission, relevant GMP templates, etc | Further information required – progress separately |  |  | Is a procedure required?
|  | Clause 4.1.3 | Clarification: Does not specify who is responsible for submitting the CTP, assume it is the generator. | Decision point for EPWA: take existing drafting to public consultation or revise drafting or discuss further prior to public consultation. |  |  | Amended to state this is the generator.
|  | Clause 4.1.3 | Recommendation: The submission/approval/revision process would be best served by an ISO procedure covering the lower level details (timing, email addresses, etc), as well as any relevant templates | No change |  |  | Is a procedure required?
|  | Clause 4.1.3(a)(vi) | Recommendation: Wording could be clearer here on what the conditions represent. Assuming these are intended to cover conditions that the generator requires to be met in order to conduct the tests (e.g. NSP lines in service, minimum demand levels, etc)? | No change |  |  | No change.
|  | Clauses 4.1.3(a)(4) - (5) | Recommendation: These two clauses reference the “controller” as the body that has the requirement, elsewhere in the clause it is the generator. Suggest keeping consistent for clarity. | Further information required – prior to public consultation |  |  | Clarified throughout to indicate that it is the controller who has the obligation, not the equipment(generator).
|  | Clause 4.1.3(b)(3) | Clarification: Should this be “unless otherwise agreed by the ISO” or NSP? | Further information required – prior to public consultation |  |  | Amended to ISO.
|  | Clause 4.1.3(b)(4) | The submission/approval/revision process for pre-test procedures would be best served by an ISO procedure covering the lower level details (timing, email addresses, etc), as well as any relevant templates Also should the reference to Procedures instead “pre-test procedures” instead? | Further information required – prior to public consultation |  |  | Is a procedure required?
|  | Clause 4.1.3(h) | Note: Currently 4.1.3(e) does not use the term direction | Drafting choice for EPWA. Should it be changed to "condition"? |  |  | Amended to 'test conducted under'.
|  | Clause 4.1.3(j) | Recommendation: Should perhaps just be a reference to all connection points, rather than just “new” connections points? | Further information required – prior to public consultation |  |  | Amended to remove word 'new'.
|  | Clause 4.2.2.A | Clarification: There is some potential for confusion here around where the approval to generate/generator monitoring plan applies - e.g. does it apply at the facility level or the generating unit level? If at the facility level, there may need to be some clauses included to deal with augmentations to the facility and permission to generate/compliance monitoring of a generating unit “within” a facility | Further information required – prior to public consultation |  |  | Generating unit.
|  | Clause 4.2.2.A | Clarification: No discussion in here on treatment of existing generators, e.g. Will existing generators be issued with Approval to Generate Notifications if they do not already have them? Will existing facilities need to produce test reports and models and have an approved generator monitoring plan if they do not already? If so, a transition process will also need to be created to cover agreement of relevant standards and allow sufficient time to develop the necessary artefacts | No change |  |  | GF discussion / Issue Lead to consider and advise in first instance.
|  | Clause 4.2.2.A€ | Another condition that may make sense to allow for is final approval of the GMP – i.e. interim approval is granted, subject to approval of the GMP by date ‘x’ | No change |  |  | Left to ISO discretion.
|  | Clause 4.2.2A(e)(2) | Clarification: Currently there are no “registered generator performance standards” in HTR context, should this just read “applicable technical standards” instead? | Further information required – prior to public consultation |  |  | Amended.
|  | Clause 4.2.2A(f) | Recommendation: Suggest changing “immediately” to “as soon as is reasonably practical” to allow time for the controller to deal with any immediate safety or power system security/reliability issues | Further information required – prior to public consultation |  |  | Amended as suggested.
|  | Clause 4.2.2A(f)(2)(ii) | Clarification: Believe renegotiation of a technical standard is not possible under the current HTR? | Further information required – prior to public consultation |  |  | Amended to refer to existing exemption process in Rule 57. Issue lead to check.
|  | Clause 4.2.2A(h) | Believe this should be and rather than or, i.e. "where the NSP and the ISO agree the controller responsible for the generating unit or generating system will be able to meet and comply with an alternative standard and technical level of performance that would not impede or risk power system security and reliability" | Further information required – prior to public consultation |  |  | Clause 4.2.2A(h) not required.
|  | Clause 4.2.2A(i) | Clarification: Is it the intention that the approval to generate notification be the official artefact that records the relevant technical standards that the generator must comply with? If so, 4.2.2A should be amended to include this requirement. An alternative would be for the NSP to create and maintain a register of relevant technical standards for each generator (which would also need its own clause) | Further information required – prior to public consultation |  |  | Amended to require NSPs to create and maintain a register.
|  | Clause 4.2.2A(j) | Clarification: Are there situations where it may make sense for the ISO to revoke an approval to generate notification as well? Also for clarity, suggest deeming that an interim approval to generate notification is revoked when an approval to generate notification is issued | Further information required – prior to public consultation |  |  | Amended.
| APA | Issue 13 | The current rules require the generator to submit materials for both NSP and ISO review. The proposed change represents a significant shift in responsibility and materially alters the risk profile for the NSP, whose assets are directly affected but who would no longer have the ability to manage that risk. The drafting also omits the NSP from the commissioning test plan process, despite the fact that the NSP must approve the connection and rely on the test results to be satisfied that the facility can operate within network performance limits. Excluding the NSP from involvement in the development and oversight of the test plan is inconsistent with the broader provisions in this section, which place explicit reliance on test outcomes as part of the NSP’s approval process. New drafting also has the ISO being responsible for compliance monitoring programs where this is an existing responsibility for NSP in clause that are not proposed as being amended. Based on this, we suggest drafting be revisited and resubmitted to the working group for review. Refer to comments provided for individual clauses. | Further information required – prior to public consultation |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.1.3(a) | The NSP must rely on the test outcomes in order to approve the generation connection as per remaining clauses. The test plans should therefore be provided to the NSP either for comment or approval to ensure a streamlined approach. |  |  |  | Amended so that the ISO must seek comments from NSP before approving.
|  | HTR 4.1.3(a)(vii) | Clarify the use of “dispatch interval” within this clause. There are no defined dispatch intervals in the rules, however this may be amended to consider any balancing periods. |  |  |  | Removed 'dispatch intervals'.
|  | HTR 4.1.3(b)(1) to (6) | Clauses should be referred to check references to “generator” versus “controllers. Clauses 4.1.3(b)(2) and (6) place obligation on ISO where NSP is required to rely on tests to approve connection. Assuming this is a drafting error, recommend updates to provide for NSP role as appropriate. Recommend discussion in working group to clarify and for the drafting to come back to the working group following amendment. |  |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.1.3(b)(4) | As per other comments, address confusion on ISO and NSP roles. Noting the increase in time period for approval changes from 30 days to 60 business days, APA recommends the working group to give consideration to the timeframes given across the testing provisions to ensure these are balanced and can be updated closer to testing periods if required. |  |  |  | Deleted 60 BD / pre-test notification requirement completely.
|  | HTR 4.1.3(c) | Noting confusion on ISO and NSP roles, does there need to be an equivalent clause enabling interim approval by the NSP? |  |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.1.3(c) | This existing clause deals with negotiation of compliance monitoring programs between the NSP and generator. New draft clauses (particularly 4.2.2A(b)(5) appears to conflict with this drafting. |  |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.1.3(d) and (e) | Noting confusion on ISO and NSP roles, update drafting to ensure NSP performance standards or outcomes are not compromised. |  |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.1.3(f) | As per other comments, address confusion on ISO and NSP roles for clauses 4.1.3(f)(i) and (ii). |  |  |  | Issue lead question - balance of responsibilities.
|  | HTR 4.2.2Ah) and (i) | Concept of negotiated performance is not a feature of the PNR and HTR. Recommend drafting be updated to align with exemption framework. This clause may impose undue costs on the connecting party where equipment is already installed and performance deviates for an unforeseeable reason. In these cases, the previous performance standard in the clauses may not be achievable and the exemption framework should be used. |  |  |  | Amended to refer to existing exemption process in Rule 57. Issue lead to check.
|  | HTR 4.2.2A(j) | As per other comments, address confusion on ISO and NSP roles. It may be appropriate for NSP to recommend revoke of interim approval or the ISO to make this recommendation to the NSP (as appropriate once roles are clarified). |  |  |  | Issue lead question - balance of responsibilities.
|  | PNR 166 | Commissioning or testing are included as a “Notifiable Event” under PNR 166. Suggest confirmation the updated clauses are still able to be considered under this definition. |  |  |  | Issue lead to consider.
| Confidential Submission | Clause 4.1.3(b)(4) | Recommendation: Applying the 60-business-day pre-test procedure submission requirement as a default is excessive and may lead to unnecessary delays in commissioning and project delivery. The submission requests that the submission timeframe should reflect the actual time ISOCo requires to undertake its review, and that an appropriate duration should be agreed with ISOCo on a case-by-case basis under “or as otherwise agreed”. Additionally, the submissions requests explicit guidance on when reduced timeframes will be accepted (including decision criteria and response timeframes) and transitional provisions for projects already underway. | Further information required – prior to public consultation |  |  | Deleted 60 BD / pre-test notification requirement completely.
|  | Clause 4.1.3(a)(3)(iii) | Recommendation: The Commissioning Test Plan requires “details of any contracts or agreements relevant to testing activities”. The submission does not consider it appropriate for ISOCo to have access to commercially sensitive contract information and requests that the requirement be removed or limited to a high-level description of testing arrangements and responsibilities (excluding commercial terms). | Further information required – prior to public consultation |  |  | Issue lead to consider policy question raised. Note the CI draft amendment (drafted so as to be subject to the PNR's sub-chapter 11.2 on Confidential Information).
|  | Clause 4.1.3(a)(4) | Recommendation: The clause states that no revised commissioning activities may proceed until ISO approval has been obtained. Commissioning plans commonly change throughout the commissioning process, and it is unclear which changes require follow-up ISO approval. In a dynamic commissioning environment, this could introduce unnecessary delays. The submission requests that only material changes require ISO approval, and that NSPs have flexibility to determine materiality; in most cases, a notification to ISOCo should be sufficient for non-material changes. | Further information required – prior to public consultation |  |  | Issue Lead to advise. See clauses 4.1.3(a)(3),(4) and (6) in draft amendment rules.
|  | Clause 4.1.3(a)(5) | Clarification: The controller must notify ISO prior to making any material change to control, protection or inverter parameters during the commissioning test period. Parameter updates are common during commissioning to achieve compliance. The submission requests clarification on what constitutes a material change and how ISO will make an informed risk-based decision (including expected response timeframes) to avoid delays during commissioning. | Further information required – prior to public consultation |  |  | Issue Lead to advise. See clauses 4.1.3(a)(3),(4) and (6) in draft amendment rules.
| Woodside | Issue 13 | The concept of interim approval, though can be understood, will add cost and time and additional risk, particularly with no tangible definition of non-compliance. | No change |  |  | Noted.
Issue 18 Issue Lead: Lekshmi (BP) | BHP | Clause 1.5 | Recommendation: The definition of dead band could be clearer, suggest referencing frequency specifically in the name and changing to something simpler e.g. (Frequency Dead Band: means the range of power system frequency for which a change in a generating unit’s active power output in response to power system frequency is not required |  |  |  | Actioned - Suggested definition adopted.
| ISO | Clause 1.5 | Recommendation: Replace definition of damping ratio. Currently, it is the definition of current transformer, which is incorrect |  | Agree |  | Actioned
|  | Clause 3.3.4.4(d) | Clarification: System? |  |  |  | Not adopted. Definition refers to unit.
|  |  | Recommendation: Drafting Instructions - 2024.08. 28 - "the conditions that may lead to an adjustable dead band being agreed to within an access contract should either be clarified, or this caveat removed.” |  |  |  | Actioned. Latest instructions were to remove the caveat.
| APA | Clause 3.3.4.4(d) | Recommendation: APA agrees with the policy intent but it’s unclear what “0.05 Hz” refers to i.e. a total dead band width of 0.05 Hz (+/- 0.025 Hz) or +/- 0.05 Hz. Suggest updating drafting to clarity this is 0.05 Hz total. This would align with updates being proposed in the subsequent sections of the HTR. |  |  |  | Actioned - No change. +/- 0.25 is used.
Issue 22/I2025.06 Issue Lead: David (HP) / Peter (ISO) | HP | Clause 3.3.4.6(a) | Recommendation: Removing 3.3.4.6(a) because the clause is no required in the technical rules | EPWA to consider whether clause 3.3.4.6(a) is necessary and potentially remove if it is redundant. | Remove only wording in clause 3.3.4.6(a) which pertains to cost recovery. Cost recovery should be covered in the PNR not the PHTR. ISO - Agree. I think EPWA can consider 3.3.4.6(a) for removal if it is redundant. |  | Actioned - removed, as suggested.
| BHP | Rule 141(2) | Recommendation: Is the intent of this to mean the ISO must consider the costs of compliance and seek to minimise as much as practically possible? If so, suggest some alternative words to clarify e.g. “In developing the Metering and Measurements Procedure, the ISO must consider and, so far as is practicable, seek to minimise compliance costs” | EPWA to review the structure of their drafting. | Agree in principle |  | Actioned - adopted wording as suggested.
|  | Rule 148A(3) | Clarification: Is this intended to cover specifications for high speed data recorders as well? Suggest it should be broadened to include this to provide certainty on the specifications for the types of equipment that can be installed to meet the requirements under 3.3.4.6 | Further information required - prior to public consultation | Suggest specifications are covered in a separate procedure |  | Broadened to include in the Metering and Measurements Procedure.
|  | Rule 148B and Clause 3.3.4.6(a) | Clarification: Seeking clarity on the obligations and cost recovery arrangements. The obligation is on a controller of a power station to install HRDR when directed by the NSP, but the cost recovery arrangements under 148B are for the NSP to recover costs. Is the intention that the controller passes the costs on to the NSP who then passes the costs on to network users? If so, the clauses need to be adjusted to clarify this | Further information required - prior to public consultation | Suggest cost recovery is dealt with in the PNR and not in the PHTR. The PHTR must make the obligations clear and PNR can cover cost recovery. |  | Amended draft text to clarify that the controller, who incurs costs, can recover from the NSP in accordance with the terms of its relevant access contract or otherwise by agreement.
|  | Clause 3.3.4.6(b)(2) | Recommendation: Suggest changing to reference the requirements published under 148A(3) per above comment | EPWA to consider whether a reference to PNR is necessary in HTR or redundant. | Suggest cost recovery is dealt with in the PNR and not in the PHTR. The PHTR must make the obligations clear and PNR can cover cost recovery. |  | No change made.
| ISO | Rule 148A(2) | Recommendation: Refer to edits to the alternative definitions of High Resolution Data and High Resolution Data Recorder provided in ISO Comments Word the new rule such that ISO and registered NSPs have discretion over what measurements they include in the above rule. This is necessary to avoid an obligation to capture all possible measurements we may request, many of which may not warrant definition in the Procedure due to their infrequent use. | Amend as suggested | Agreed |  | Amended as suggested.
|  | Clause 1.5 | Recommendation: I’ve tried to remove the ambiguity from original AEMO definition. ISO believes that 20 milliseconds (aka 50Hz) refers to the reporting interval of processed data from the device to the database, not the underlying sampling of raw voltage/current which must occur at a much higher frequency (multiples times per period) to accurately estimate the magnitude and phase of the 50Hz sine wave. Unfortunately, “High Resolution Data Recorder” cannot be defined as an extension of AEMO’s “High Resolution Data” definition as it becomes circular: the High Resolution Data definition already includes PMUs and high speed monitoring devices in itself. Proposed drafting [edits underlined in green]: High Resolution Data: Means data measured and transmitted to the ISO in near real time by devices with GPS clock synchronisation (or equivalent technology) and a typical reporting interval of 20 milliseconds, allowing for accurate representation of power system behaviour, including during transient events, including: - Measurement of system frequency and electrical time; and - Data measured by phasor measurement units and other devices that is transmitted for real time operational purposes. High Resolution Data Recorder: Means a device (such as a phasor measurement unit or other type of device specified under the PNR from time to time) that produces High Resolution Data in accordance with the applicable requirements of the PNR. | Further information required - prior to public consultation | Agreed |  | Amended as suggested.
|  |  | Clarification: Issues paper recommended to add synchrophasors, not sure if intentional to be left out. (Refer to definition of Point of Common Coupling in provided comments) | Further information required - prior to public consultation | Agreed |  | No change. Not included in Dis.
| APA | Rule 148A(2) | Recommendation: Supports change but this change should seek to accommodate or align with existing metering obligations (including existing legislative gaps). It may be prudent to time obligation for the ISO to produce the Procedure with planned reforms to metering being considered as part of the PNR reforms if it is to include this data. | Further information required – prior to public consultation | ISO - There is a lot here (and below). EPWA may need to make a call whether further engagement is warranted before progressing to public consultation. |  | r148A(2) provides ISO with discretion and flexibility, intended to support efficiency.
|  | Rule 148A(1)(a)(iii) | Recommendation: Under subchapter 5.2 of the PNR, the ISO publishes reference nodes and NSP’s determine and publish loss factors. Suggest drafting is updated to avoid misunderstanding on roles and responsibilities. Proposed drafting [edits underlined in green]: to undertake Loss Factors functions under Subchapter 5.2. | Further information required – prior to public consultation |  |  | Change adopted.
|  | Rule 148A(1)(b) | Recommendation: Development of the processes should consider when measures defined in the HTR are not required and where measurement can be deterred via alternative methods such as inference. Further, shared data sources, such as where high speed recording is being used for both network and generator performance monitoring should be recognised. Proposed drafting [edits underlined in green]: (ii) identifying circumstances when data and measurements defined in the HTR are not required or may be inferred via means other than installation of RME or high resolution data recorders. Interaction with existing systems is not clear. Treatment for existing systems and those under development should be considered by the working group and potentially deemed compliant where appropriate. | Further information required – prior to public consultation |  |  | Added new r148A(1)(b)(iii) to address.
|  | Rule 148A(2) | Recommendation: A complementary clause should be included to provide a mechanism for measurements that ISO and NSP may agree are not required (but might otherwise be considered standard). This would provide balance and recognise the NWIS operates efficiently where duplication and unnecessary information exchange is avoided. A relevant example here is high speed recording that is capturing both network and generator performance. Clear head of power is required to facilitate continued efficient operation and management of the systems. | Further information required – prior to public consultation |  |  | Change incorporated.
|  | Clause 3.3.4.6(c) | Recommendation: If the ISO is directing NSPs to direct Controllers, it would be appropriate for it to state the reasons for this and what the new installation is required for. There should also be the ability for the NSP to respond. This may avoid situations where the ISO requirement is being driven by perceived lack of data rather than a material requirement to install new equipment. Proposed drafting [edits underlined in green]: (3) The ISO notice to an NSP or controller under clause 3.3.4.6(c) must clearly specify the circumstances in which the data is required, the implications for power system security (including the relevant rule provisions relied upon by the ISO), and identify any events or conditions that led to the ISO’s decision. | Further information required – prior to public consultation | Agreed in principle. |  | Added clause 3.3.4.6(d) to address.
|  | Clause 3.3.4.6(d) | Clarification: if these provisions should be simply included within the definition of high resolution data rather than a rule clause? Note that typically high speed recorders would not measure MW or MVAr, rather they measure current, voltage and frequency and then calculate MW and MVAr. | No change | Suggest some level of explanatory context is useful (inclusion of typically monitored variables) as written or as an introductory paragraph to 3.3.4.6 |  | Clauses 3.3.4.6(c)(1) and (2) amended to address distinction.
| Confidential Submission | Rule 141, 148, 148A & 148B | Recommendation: The draft expands ISO data specifications/exchange protocols and introduces processes for implementing remote monitoring equipment and high-resolution data recorders. The submission supports the intent, but requests that a separate guideline be provided that sets out: (1) minimum functional requirements (data points, availability/latency, retention and security), (2) a risk-based prioritisation and staging framework, (3) transitional arrangements for existing facilities and in-flight projects. | No change | Agreed in principle. ISO - recommend no changes. ISO already has to align its functions with the efficiency requirement of the PEO. The greater risk is delaying high speed data recorders. |  | The ISO function must align with PEO. The Procedure Change Process should ensure these aspects are considered and reflected in the ISO's data requirements. A guideline would not add further value.
|  | Clause 3.3.4.6(c) | Recommendation: The clause allows the ISO to direct the NSP to issue and implement a notice requiring the installation/upgrade of high resolution data recorders. The submission requests that this clause be clarified to include a risk/value-based decision framework (including an “equivalence” option where existing data is fit-for-purpose), consultation with the NSP prior to direction, and clear cost allocation/recovery arrangements where additional equipment is required. | No change | Agreed in principle, particularly around NSP consultation and consideration of suitability of existing available data. Any detailed framework information should be containted within an ISO procedure. Any cost recovery arrangements should be dealt with in the PNR. ISO - recommend no changes. ISO already has to align its functions with the efficiency requirement of the PEO. The greater risk is delaying high speed data recorders. |  | Amended to include requirement that ISO consults the relevant NSP before issuing a notice. Cost allocation is outlined in 148B.
Issue 23/I2025.02 Issue Lead: David (HP) / Peter (ISO) | BHP | Clause 3.3.3.1(c)(1) | Recommendation: The reference to generating unit should be generating system or facility to capture other reactive power devices that are supporting the generating unit to meet the requirement (e.g. STATCOM/SVC) | Further information required – prior to public consultation | No the generating unit itself must comply. If it can't comply (and if for example a STATCOM is to be used to achieve compliance) other mechanisms such as connection point compliance, derogations or negotiated outcomes would need to cover this situation. |  | No change. The generating unit itself must comply. If it can't comply (and if for example a STATCOM is to be used to achieve compliance) other mechanisms such as connection point compliance, derogations or negotiated outcomes would need to cover this situation.
|  | Clause 3.3.3.1(c)(2) | Recommendation: Believe the reference to minimum active power output level should be maximum loading level (or similar) to capture -ve active power range (MW Absorb range) in the chart. Also sub-parts (A) and (B) could be combined into a single clause as per part (1) | Further information required – prior to public consultation | 3.3.3.3(c)(2) does not refer to minimum active power output level. Suggest no change. ISO - comment is unclear to me. May require further consultation |  | Amended claused 3.3.3.1(c) (2) to replace 'minimum active power output level' with 'minimum active power absorption level'.
| ISO | Clause 3.3.3.1(c)(1) | Recommendation: Full agreement with the intent of this clause. However, while this clause is very concise, it may be unclear how it is intended to apply to Generating Units vs. energy storage devices. Including separate figures for Generating Units and energy storage devices may reduce ambiguity. Noting that clarity/certainty of requirements is highly valued by generators/NSPs. | Further information required – prior to public consultation | Agreed - provide separate figure for Energy Storage Facility |  | Separate figures introduced.
|  | Clause 3.3.3.1(c)(2) | Recommendation: Replace energy storage devices with Storage Facility for consistency with other clauses in HTR e.g. 3.7. | Further information required – prior to public consultation | Agreed - use Energy Storage Facility |  | Amended
|  | Figure 3.1 | Recommendation: Minor formatting issues in drawing. (See alternative provided) - MW Supply and MW Absorb labels on vertical axis - MVAr supply label off centre - Diagram is a bit warped. Should be 1:1 | Further information required – prior to public consultation | Agreed |  | Amended
|  |  | Recommendation: Generating Unit is unlikely to have MW absorb capability. Replace with Energy storage device / Generating Unit | Further information required – prior to public consultation | Agreed (see above) - provide separafe figure for Energy Storage Facility |  | Amended
| APA | Clause 3.3.3.1(c) | Recommendation: Consider treatment for existing generation facilities or deeming compliance. Alternatively, if the performance degrades for unforeseen reasons. Unclear if the rules clarify the conditions under which generating units may be unable to meet the reactive power requirement of 0.484 (48.4%) of active power. In such cases, the participant may need to negotiate an agreed performance outcome with the NSP. This is particularly important for existing generating units and for operation under extreme hot conditions, where units may be derated and unable to maintain full reactive capability. | Further information required – prior to public consultation | Suggest this should be covered in Section 1 general conditions of the rules and treatment of grandfathering and performance degredation. These general principles would apply across a range of technical requirements and grandfathering shouldn't be dealt with in any one particular clause. Action: Check general grandfathering clauses. |  | Grandfather discussion
|  | Figure 3.3 | Recommendation: The updates to Figure 3.3 need to clarify which applies when charging or discharging. Suggest adding text to clarity. Alternatively, revert to the two-quadrant approach with one figure for charging and one for discharging. | Further information required – prior to public consultation | Agreed (see above) - provide separate figure for Energy Storage Facility |  | Updated Figure (now 3.2) which hopefully provides clarity.
| Confidential Submission | Clauses 3.3.3.1(c)(1) - (2) and Figure 3.3 | Recommendation: Tightens inverter reactive capability from ±0.95 pf to ±0.9 pf, increasing required Mvar support from the inverter-based plant. This change may increase inverter MVA headroom and/or add additional inverter capacity (more inverter blocks) to meet the connection point's reactive capability, with material and delivery impacts. The submission requests that the requirement be applied on a connection point basis and be study-driven, such that the required reactive capability/power factor at the connection point is set based on power system studies (voltage control needs and network capability). This would ensure the requirement is proportionate and avoids over-specifying inverter capacity where existing capability is sufficient. | No change | The changes align with the WEM rules and equipment capability and long term objectives for the Pilbara Grid. Suggest a negotiated outcome or derogation could be utilised to deal with specific project limitations. Action: Check general derogation and negotiation clauses. ISO - No changes. +/- 0.9pf is consistent with working group intent. The anonymous submission holds no value as they are unwilling/not-present to defend their opinion. |  | The current position reflects a consensus in HTR working group discussions.
|  | Clauses 3.3.3.1(c)(1) - (2) | Clarification: The clause uses a 0.484 multiplier to set reactive power capability, but the factor is not defined (unitless) and appears in multiple clauses. The submission requests clarification of what 0.484 represents (and its basis) and includes an explicit definition/explanatory note for consistent interpretation. | N/A - not lead | Agreed - provide explanatory footnote ISO - No changes. 0.484 is very obviously the factor required to achieve 0.9pf. Its units are MVAr / MW. HTR are written to be read and applied by engineers and should not be cluttered with explanation for lay readers. |  | This clause reflects existing convention in current clause. 0.484 is the fixed coefficient (constant) that represents a required ratio between reactive and active power. It implies a power factor of roughly 0.9.
Issue 24 Issue Lead: David (HP) | HP | Title of Clause 3.4 | Recommendation: Remove the words "to the distribution network" in order to cover generators <10MW connected to the transmission system" |  | Agreed |  | Amended.
| BHP | 3.3.3.1(a) | Recommendation: The updates to the note tend to place an obligation on the NSP, suggest this should be part of the clause rather than part of the note. |  | Agreed |  | Amended.
|  | Table 3.1 | Recommendation: Note 5 needs to be added to the right hand column of the table along with the references to the other notes |  | Agreed |  | Amended.
| ISO | Clause 3.3.3.1(a) | Recommendation: It is a risk to have a direct dependency on the AEMO guideline in the HTR, noting AEMO has no role in the NWIS. It may be safer to incorporate a snapshot of the existing methodology into the NWIS framework, e.g. through an HTR appendix. I also note the methodology in section 3 of the guideline refers to AEMO and Market Participants which aren’t defined under the NWIS framework. So the roles and responsibilities for applying the methodology are ambiguous. The methodology should be adapted to the NWIS context. |  | Agreed - remove reference to AEMO guideline, and update to "… site specific maximum ambient temperature as determined by the NSP with a 1% probability of exceedance during the Hot Season, or 50 degrees….." |  | Amended note, removing reference to AEMO guideline and, update to, "… site specific maximum ambient temperature as determined by the NSP with a 1% probability of exceedance during the Hot Season, or 50 degrees….."
| APA | Chapter 8 | Recommendation: APA seeks clarity on clauses where the term “Hot Season” may be used beyond the note under clause 3.3.3.1. Noting the suggestion below, the definition may be unnecessary. |  | Appears it is only used for the purposes of establishing a temperature reference for reactive power capability temperature dependence. |  | Amended note, removing reference to hot season.
|  | Clause 3.3(a) | Clarification: From a technical perspective, using temperature capability curves as a reference to determine the Active and reactive power a generating unit can provide at a given ambient temperature (including Hot Season defined above), accounting for temperature-related derating. This would enable more accurate prediction of the generating unit’s response and performance under varying temperature conditions. |  | Yes this would be a suitable method but not necessary to define this in the rules. |  | Agree with Issue Lead, "Yes this would be a suitable method but not necessary to define this in the rules."
|  | Clause 3.3.3.1 | Recommendation: Rather than relying on an AEMO method that does not directly consider the Pilbara, it may cleaner to fix temperature at 50 degrees. This would simplify drafting and potentially avoid introduction of a new term “Hot Season”. |  | Note above and removal of reference the AEMO guideline. The 1% POE is retained however as it allows greater flexibility for proponents, at suitable risk level. |  | Amended note, removing reference to AEMO.
|  | Table 3.1 + Clauses 3.4 & 3.5(e) | Recommendation: As per comment on PNR 3.3(a) above, it may be prudent to use temperature capacity curves for accuracy. |  | See comment above |  | Agree with Issue Lead, "Yes this would be a suitable method but not necessary to define this in the rules."
| Confidential Submission | Clause 3.3 | Clarification: The requirement to use “nameplate rating” for generator classes and technical requirements is unclear. Generator nameplate may differ from prime mover/inverter/package capability and can vary with reference conditions (e.g., temperature/altitude/derating). The submission requests that you clarify which rating basis applies (generator, prime mover, or inverter/package) and the reference conditions to be used for classification/compliance. |  | Suggest a definition of 'Nameplate rating' is added, which would be the nominal rating of the generator taking into account the most limiting factor (generator, prime mover, inverter/package). ISO - No changes are necessary. Why are they mentioning the prime mover at all? The confidential submission should establish there is an existing problem before we expend effort making changes. |  | Nameplate rating' is defined in the HTR. Notes amended to clarify reference conditions.
Issue 26 Issue Lead: David (HP) | BHP | Clause 3.4.9 | Recommendation: If the proposed changes to this clause are seeking to make this requirement common for all generators, then the clause needs to be moved outside of this section as this section (3.4) is only relevant to generators <10MVA |  | The proposed changes to clause 3.4.9 are only applicable to generators <10MVA as covered in section 3.4. The changes seek to remove the dependency of the clause on export levels (and acknowleges there may be generators <10MVA which are connected to the transmission system). |  | The proposed changes to clause 3.4.9 are only applicable to generators <10MVA as covered in section 3.4. The changes seek to remove the dependency of the clause on export levels (and acknowleges there may be generators <10MVA which are connected to the transmission system).
|  | Clause 3.5.1(a) | Clarification: Assume installations rated >1000kVA are not permitted on the low voltage distribution system? (currently not stated) |  | The PHTR does not prohibit the connection of installations >1000 to the low voltage distribution system. |  | The PHTR does not prohibit the connection of installations >1000 to the low voltage distribution system.
|  | Clause 3.5.2(a) | Clarification: Believe this should be “a generator must provide for” rather than a generating unit |  | Agreed |  | Change adopted as suggested.
|  | Clause 3.5.2(a) | Clarification: Is the intent of this clause to cover very small generating systems on the low voltage distribution system? I.e. should rooftop solar installations have to meet this requirement? If so, is this intended to be retrospective? |  | Yes. The intent is to cover small (<1000kVA) generating systems on the distribution system, including rooftop solar installations. Normal grandfathering principiles should apply - i.e. this requirement is not retrospective. Action: Check general grandfathering clauses. |  | Yes, covers rooftop solar on distribution system. Grandfathering to be discussed
| APA | Clause 5.9.2(a)(4) & 5.9.2(e) | Recommendation: Remove reference to facsimile numbers as this is an outdated form of communication. |  | Agreed |  | Amended.
| Confidential Submission | Clause 3.5.2 | Recommendation: Requires LV inverter remote trip/remote real power control and remote monitoring (MW, Mvar, V) from the NSP control centre. This submission is not supportive as drafted because Participants in the NWIS may not currently have LV monitoring/control infrastructure at scale, and compliance would require significant new investment (comms, SCADA/OT integration, cybersecurity and likely a DERMS-style platform) for limited operational value in remote networks. |  | This is a key requirement to management of low loads and renewable intermittency on the system, and is forward looking only (Existing systems would be deemed to comply). Action: Check general grandfathering, derogation and negotiation clauses cover potential unique situations in remote parts of the network where these issues are either pre existing or can be managed by alternative solutions. |  | WG to discuss if investment is required to implement, and if requirements would be grandfathered.
Issue 28 Issue Lead: David (HP) | HP | Table 3.1 | Recommendation: Identified Typo in new Table 3.1 (22kV instead of 220kV) |  | Agreed |  | Amended.
| BHP | Clause 3.2.1(f)(3) | Clarification: We think the concept of “new equipment” should be defined, e.g. is the intent to cover anything installed after a particular HTR revision date, including like-for-like replacement of existing assets, etc? |  | Agreed - add a clarifying note to define new equipment and point to grandfathering clauses for pre-existing equipment. |  | WG GF discussion
|  | Clause 3.2.1(f)(3) | Clarification: is the intent to cover equipment below the connection point as well? |  | Yes |  | Yes, this is the intent.
|  | Clause 3.4.6(a) | Clarification: Not clear why this clause is subject to 3.2.1(f) |  | Agreed - suggest remove the reference to 3.2.1(f) which is not critical. |  | Amended.
| APA | Clause 3.2.1(f)(3) | Recommendation: It may be worth clarifying what “new equipment” means in a HTR context and removing or updating these references to include a clear effective date or consider as part of generalised provision holding performance constant as at time of installation (for example). It may the use of “new equipment” elsewhere in the HTR is a feature of drafting left over from older versions of either the Western Power or Horizon Power Technical Rules (on which the HTR is based). The equivalent clause in the Western Power Technical Rules (2016) is 2.9.4(i) states: “The term "existing equipment" refers to equipment in service at the Rules commencement date.” An equivalent clause does not seem to appear in the HTR. |  | Agreed - add a clarifying note (see above) |  | Amended wording to replace 'new' with 'equipment commmissioned after [date] must meet or exceed'. This reflects the policy intent is simply to to distinguish existing assets from future assets.
|  | Table 3.1 | Recommendation: Table refers to the “transmission system” but includes voltages that are considered “distribution”. Recommend any table does not include below 33 kV (noting 33 kV could be used to support transmission). |  | 22kV and 11kV can be used to suppor transmission (eg reactor and capacitor bank connections within transmission substations) |  | Left as is - 22kV and 11kV can be used to suppor transmission (eg reactor and capacitor bank connections within transmission substations)
|  |  | Recommendation: Ratings for 330 kV down to 66 kV are aligned with IEC 62271-100 (2021) subclause 4.101.1 and are typically preferred values that manufacturers use globally so unlikely to cause procurement issues. Values provided for 33 kV and below. These values look conservative. We recommend the value for 33 kV be 25 kA rms not 16 kA rms. As above, recommend removing values for 22 kV and 11 kV from the transmission system table. |  | These values (for 33kV and below) can be considered minimum plant ratings (so do permit installation of higher rated equipment). Suggest retaining value of 16kA at 33kV as a minimum requirement. |  | These values (for 33kV and below) can be considered minimum plant ratings (so do permit installation of higher rated equipment). Suggest retaining value of 16kA at 33kV as a minimum requirement.
|  | Table 3.2 | Clarification: Seek clarity on the use of a 13.1 kA limit for 33kV. This could be based on the legacy 750 MVA limit, is there a specific network constraint keeping us at this number? It might be cleaner for standardising new connections to bump this to 16 kA to align with the IEC 62271-100 and simplify equipment procurement? |  | Horizon Power note - we looked at this (increasing 33kV to 16kA) in the context of our distribution equipment purchasing and this would cause some issues hence leaving at 13.1 as a minimum. |  | Response from Issue Lead:Horizon Power note - we looked at this (increasing 33kV to 16kA) in the context of our distribution equipment purchasing and this would cause some issues hence leaving at 13.1 as a minimum.
| Confidential Submission | Clause 3.2.1(f) & Table 3.1 | Recommendation: Table 3.1 (equipment connected to the transmission system) lists “22 kV”, which appears inconsistent and is likely intended to be “220 kV”. The submission requests confirmation or correction of this reference to avoid misinterpretation and inappropriate equipment specifications. This submission also requests flexibility on the short-time withstand requirements for 220 kV and 132 kV equipment. Specifically, where prospective fault level studies demonstrate materially lower fault levels at the installation point, the NSP should be able to specify a lower equipment rating. |  | Note comment above regarding typo and correction of the 22kV reference to 220kV. Action: Check general derogation and negotiation clauses to cater for situations where long term prospective fault levels at points in the network are significantly lower than the minimum ratings. |  | WG GF discussion / Flexibility
|  | Clause 3.4.6(a) & Table 3.2 | Table 3.2 sets minimum short time withstand and breaking current ratings for distribution equipment. The submission requests that the table adopt higher, more conservative minimum ratings to support future fault-level growth and site expansion (increased load and new generation). Equipment ratings can be negotiated with the NSP when fault-level calculations demonstrate materially lower prospective fault levels at the installation point. |  | These values (for 33kV and below) can be considered minimum plant ratings (so do permit installation of higher rated equipment). |  | Open question for Issue Lead.
Issue 29 Issue Lead: Peter (ISO) | ISO | Explanatory Note | Clarification: Drafting Instructions - 2024.11.14 - “It is recommended to explore a requirement in the PNR or HTR mandating at least one network synchronisation point, capable of synchronising the two networks, on every interconnector between networks of registered NSPs and CPC Facility Networks." | Further information required – prior to public consultation |  |  | Current drafting insutrctions do not outline how this consideration would be drafted.
Issue 32 Issue Lead: Peter (ISO) | BHP | Clause 2.6.4(i) | Recommendation: While the NSP/ISO may agree to a higher clearance time based on network conditions, they should also have the ability to require the clearance time to be reduced to the required levels in table 2.10 should network conditions change. | Further information required – prior to public consultation |  |  | Amended as suggested, but open question for Issue Lead. See wording in 2.6.4(i).
|  | Clause 2.6.4 + Table 2.10 & 2.11 | Clarification: We note that the alternative maximum total fault clearance time for 66kV in table 2.11 is lower (105) than the value for the maximum total fault clearance time for 66kV in table 2.10 (120). Query on what the rationale is for this? | Further information required – progress separately |  |  | Open question for Issue Lead.
| APA | Clause 2.6.4 + Table 2.10 | Clarification: It may be worth clarifying what “new equipment” means in a HTR context and removing or updating these references – perhaps as part of a separate workstream? | Further information required – progress separately |  |  | Open question for work group.
|  | Clause 2.6.4(h) | Recommendation: May be worth considering use of the word “longer” rather than “higher” in this clause given that a “higher standard” could be a shorter time. The clause appears to seeking to allow a longer time than the table (which is a number higher than the standards but not a higher standard). Proposed drafting [edits underlined in green]: The maximum total fault clearance time may be higher longer than the standard maximum total fault clearance time set out in Table 2.10, provided such change has been justified by the host NSP with reference to studies, and is agreed by the ISO. | Further information required – prior to public consultation |  |  | Amended to "longer"
| Confidential Submission | Table 2.1 | Recommendation: Table 2.10 specifies remote-end fault clearance times (incl. 220 kV, 132kV and 33 kV) that are faster and does not clearly address tie-line treatment. The submission requests that the table be aligned by adopting the worst-case (longest) time as the default benchmark. Where faster remote-end clearance is required, it should be justified through CFCT studies and agreed for the relevant network section/connection (and reflected in access contracts and compliance study assumptions). | No change |  |  | HTR outline automatic standards, not minimum standards.
Issue 35 Issue Lead: Njabulo (BHP) | BHP | Rule 198A | Recommendation: We believe the clause should include some general provisions for reviewing the ongoing adequacy of a special protection scheme once it has been installed, and requirements to revise/remove the scheme as needed |  |  | Agree | Added new clauses to reflect this.
|  | Rule 198A(3) | Recommendation: We note that the ISO can identify the need for a SPS, but that ultimately the NSP can choose to pursue the investment or disagree (outlining why no further action is required). We suggest that the ISO make the final determination based on feedback from the NSP |  |  | Agree | Question for WG - expanded policy position.
| APA | Rule 198A(2)(d) | Clarification: The note on clause 198A(2)(d) indicates the design of the scheme should look to avoid the use of ESS, constraint rules or manual load shedding measures where feasible. If these measures are available and can be adjusted to avoid the situation, should these not be considered? |  |  | Address as a separate new issue prior to finalising draft | Question for WG - expanded policy position.
|  | Rule 198A(3) | Recommendation: Special protections schemes can be quite complex, so the timeframes for assessment must be reasonable to avoid the NSP having to default to a “no further action” outcome. Suggest drafting provides a minimum timeframe for the NSP to report to the ISO, for example six months. This would allow for schemes that require plant changes and test plans etc to be mapped appropriately and the involvement of various parties to be properly canvassed before a decision on pursual is given. |  |  | The suggested timeframe seems reasonable, however, this should be taken up as a new issue with proper stakeholder consultation afforded | Left as is - 198A(3) relies on ISO discretion setting timeframe for NSP. The ISO should be trusted to set a reasonable timeframe without a minimum being specifed in the rules.
| Confidential Submission | Rule 198A(2)(d) (Note) | Clarification: The note refers to avoiding “manual load shedding” measures where feasible, but does not address automatic schemes such as UFLS and UFIS. The submission requests clarification on whether UFLS/UFIS are intended to be treated as a Special Protection Scheme under the proposed SPS/Protected Events framework, and if so, what governance, documentation, testing and reporting obligations would apply to these existing schemes. |  |  | Continue drafting and address as a separate new issue. UFLS/UFIS are a form of special protection scheme, governance, documentation, testing and reporting obligations to be addressed as a separate issue | Question for for issue lead.
Issue 40 Issue Lead: David (HP) | HP | Issue 40 | Recommendation: The approach taken to updating the standards in the HTR was not the recommended approach: > The recommended approach was to remove the year designation from all standard references, and add a covering explanatory note that “the most recent version of the standard shall apply unless otherwise indicated”. This applies to all standard references identified in the TR (not just those identified below). > Suggest wording along the lines of: “All references to Australian and international standards within this document shall be interpreted in accordance with the latest published versions of the relevant standards, unless a specific edition is explicitly stated." |  | Agreed - remove specific year references to standards in the document and add words in section 1 around the treatment of standards (latest year to apply unless indicated). |  | Removed years from referenced standards and added note to 1.5(c) .
| ISO | Clause 3.4.10.1 | Recommendation: This standard does not cover automatic transfer switches. This is an asset level standard which the ISO does not have access to. But, speaking from my own (Lewis') experience at WP this was raised as an issue by an independent consultant. NSPs may want to review and confirm. 60946.6.1: IEC 60947-6-1 - Low-voltage switchgear and controlgear – Part 6-1: Multiple function equipment – Transfer switching equipment ¦ GlobalSpec |  | Action - suggest detailed technical review of this clause and applicability of this standard. |  | Left as is - changes simply require latest version of the standards to be used. If the standard can't be accessed by industry, alternative standards will need to be identified before this is removed.
| APA | Clause 3.3.3.2 | Clarification: Clause refers to “induction generating units” should this term be updated? Is there an equivalent standard for inverter-based generation that needs to be included? |  | The clause refers to both synchronous and induction units as being relevant to the rotating electrical machines standard. |  | No change required. The clause refers to both synchronous and induction units as being relevant to the rotating electrical machines standard.
|  | Clause 3.8.6 | Clarification: Change adopts an earlier version of the standard – is this correct? |  | Agreed - the referenced version of the standard is not correct - the year reference to the standard should be removed (see note above) |  | Amended.
Issue I2025.03 Issue Lead: Peter (ISO) | BHP | Clause 3.3.4.4(e) | Recommendation: Currently no inclusion of applicable ambient temperatures for this clause as there was for reactive power response, suggest including here also to aid interpretation | Further information required – prior to public consultation |  |  | Added drafter note describing applicable ambient temperature after to end of clause 3.3.4.4€.
|  | Clause 3.3.4.4(e)(1)(A) - (B) | Clarification: The clauses specify an increase or reduction from the generating unit’s rated active power output, however believe the intention is to say ‘….be capable of achieving an increase in generator’s unit’s active power output of not less than 5% of its rated active power output for a 0.1Hz reduction in frequency…..’.? | Amend as suggested |  |  | Amended.
Issue I2025.07 Issue Lead: Peter (ISO) | APA | Clause 1.5 | Recommendation: Suggest removing reference to the (Horizon Power) Technical Rules and confirm clause references are correct within the HTR. Proposed drafting [edits underlined in green]: means the point on the network at which the NSP requires compliance with the clauses 2.3.3(a) and 2.3.4(a). Under normal circumstances this compliance is required at the connection point, but the NSP may, at its sole discretion, allow the “point of common coupling” to be at a point on the network upstream from the connection point, where it is reasonable to do so in accordance with good electricity industry practice. | This comment reflects what has been already completed on the draft - no change to amendment. |  |  | Already reflected in drafting.