## Title
This workbook has been developed for the purposes of assessing the least fixed cost candidate configuration for the draft determination of the 2026 Benchmark Technology.
It is not for use for any other purpose and is not to be relied upon by any party besides EPWA for the use of its intended purpose above.

## Parameters
Parameters
Current date | 2026-06-30
BRCP date | 2029-06-30 |  | Date the plant is assumed to be built by. BRCP costs expressed in these dollars
Fx date | 2025-06-30 |  | GHD, CSIRO and IASR values are $2025
Fx rate | 0.655
Ref date for technology costs | 2025-06-30 |  | Same as fx date
CPI index at Ref date | 98.43
CPI index at current date | 101.7
CPI index at BRCP date | 111.3868
WACC | 10.85% |  | ERA: 2026-brcp-final-determination-calculation-spreadsheet
Amortisation period | 15 |  | ERA: 2026-brcp-final-determination-calculation-spreadsheet
Tilt factor | 1
Owner's cost allowances for thermal plant | 12% |  | GHD for AEMO. Note incl land as well as owners and development costs but this is ignored as small and not dissected
Notional BESS size | 200 | MW net | Used to convert $/kW and $/kW/y parameters (from IASR) into $
Pre-FID development cost | 20 | $M | Nominal allowance. Same for all configurations
Include Fixed Capital charge? | TRUE |  | EPWA to include or exclude
Fixed Capital charge value | 100000 | $/MW | https://www.wa.gov.au/organisation/energy-policy-wa/fixed-capital-contribution-consultation
Site location | Average
Land cost | 536250 | $/Ha | Refer land tab
Proportion of installation cost that is labour | 30% |  | See TFlow33 sheet for guidance
Fixed maintenance factors (% of capex)
- Electricity connection | 0.5% |  | Jacobs
- Gas connection | 0.25% |  | Jacobs
TUOS charge parameters: |  |  | Refer WP sheet
- Use of system | 2.147 | c/kW/day
- Control system service price | 0.305 | c/kW/day
- Metering charge | 1211.979 | c/meter/day
DBNGP tariff | 1.8188 | $/GJ/day | Refer Gas sheet
Corporate overhead and consulting costs | 1312875 | $/y | GHD report 2028/29 Table 20
Insurance adjustment | 0.3% | of capex/year (excl extras which are offsite or N/A) | Added by Jacobs as we were not satisfied was in the IASR amounts adequately (referencing source GHD etc reports)
Site security | 168480 | $/y | GHD report 2028/29 Table 21
Rates | 221986 | $ per 7.3 Ha | GHD report 2028/29 Table 22
| 30409.0411 | $/Ha
Fuel stored - Gas Only case | 14 | Hours
Fuel stored - DF case | 36 | Hours | 1.5 days when distillate is the RCP fuel, allows for order lag, leaving some in tank etc
Cash cycle for WC calc | 45 | Days | Assumption
Selected technical parameters:
Configuration |  |  |  | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | CCGT | CCGT | CCGT | CCGT | RECIP | RECIP | RECIP | RECIP | BESS | BESS | BESS
|  |  |  | GT13E2 | GT13E2 | SGT5-2000E | SGT5-2000E | 1x9FA | 1x9FA | LM2500 | LM2500 | LM6000 | LM6000 | LMS100 | LMS100 | 9FA | 9FA | GT13E2 | GT13E2 | Jenbacher | Jenbacher | Wartsila | Wartsila | 6hr | 7hr | 8hr
|  | Row |  | DF | GasOnly | DF | GasOnly | DF | GasOnly | GasOnly | DF | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly
Tag |  | 1 |  | SCGT _GT13E2 _DF | SCGT _GT13E2 _GasOnly | SCGT _SGT5-2000E _DF | SCGT _SGT5-2000E _GasOnly | SCGT _1x9FA _DF | SCGT _1x9FA _GasOnly | SCGT _LM2500 _GasOnly | SCGT _LM2500 _DF | SCGT _LM6000 _DF | SCGT _LM6000 _GasOnly | SCGT _LMS100 _DF | SCGT _LMS100 _GasOnly | CCGT _9FA _DF | CCGT _9FA _GasOnly | CCGT _GT13E2 _DF | CCGT _GT13E2 _GasOnly | RECIP _Jenbacher _DF | RECIP _Jenbacher _GasOnly | RECIP _Wartsila _DF | RECIP _Wartsila _GasOnly | BESS_6hr | BESS_7hr | BESS_8hr
IASR selection |  | 2 |  | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (large GT) | CCGT | CCGT | CCGT | Gas recip | Gas recip | Gas recip | Gas recip | Battery storage (6hrs storage) | Battery storage (7hrs storage) | Battery storage (8hrs storage)
3
4
Configuration Gross MW (clean-as-new) |  | 5
Configuration Nnet MW (clean-as-new) |  | 6 |  | 341.1887 | 341.1887 | 347.773 | 347.773 | 258.2408 | 258.3028 | 380.2258 | 380.2258 | 264.0813 | 264.0863 | 356.2173 | 356.2223 | 389.5131 | 389.5811 | 489.2671 | 489.2721 | 245.7632 | 245.7632 | 217.408 | 217.408 | 200 | 200 | 200
7
HR, net, LHV, GJ/MWh (clean-as-new) |  | 8 |  | 9.771 | 9.771 | 10.057 | 10.057 | 9.61 | 9.608 | 9.392 | 9.392 | 8.98 | 8.98 | 8.72 | 8.72 | 6.319 | 6.318 | 6.818 | 6.818 | 7.836 | 7.836 | 7.868 | 7.868
Gas supply pressure at skid edge, Bara |  | 9 |  | 26.6 | 26.6 | 20.75 | 20.75 | 28.37 | 28.37 | 37.61 | 37.61 | 50.91 | 50.91 | 60.21 | 60.21 | 28.37 | 28.37 | 26.6 | 26.6 | 11.35 | 11.35 | 6.993 | 6.993
Fuel, GJ/h (on gas, approx) |  | 10 |  | 3690.4661 | 3690.4661 | 3871.7917 | 3871.7917 | 2747.2352 | 2747.323 | 3953.1867 | 3953.1867 | 2625.1952 | 2625.245 | 3438.58 | 3438.6283 | 2724.6959 | 2724.7402 | 3692.7561 | 3692.7939 | 2131.8612 | 2131.8612 | 1893.5966 | 1893.5966 | 0 | 0 | 0
11
Proportion of powerplant capex that is installation |  | 12 |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 17.12% | 17.12% | 17.11%
Localisation factor for capex |  | 13 |  | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 104.5% | 102.6% | 102.6% | 102.6%
14
# Electrical connections |  | 15 |  | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Area (powerplant excl switchyard) | Ha | 16 |  | 2.69 | 2.278 | 2.604 | 2.201 | 2.446 | 1.815 | 3.849 | 4.568 | 3.233 | 2.751 | 5.7 | 4.826 | 3.96 | 3.084 | 4.11 | 3.643 | 3.068 | 2.45 | 2.517 | 2.05 | 10.35 | 12.075 | 13.8
17
Electrical Connection Cost | $M | 18 |  | 41.5002 | 41.5002 | 41.5002 | 41.5002 | 26.5501 | 26.5501 | 41.5002 | 41.5002 | 26.5501 | 26.5501 | 41.5002 | 41.5002 | 26.5501 | 26.5501 | 41.5002 | 41.5002 | 26.5501 | 26.5501 | 26.5501 | 26.5501 | 26.5501 | 26.5501 | 26.5501
Gas connection cost | $M | 19 |  | 28.7937 | 102.6323 | 28.7937 | 95.5807 | 22.0953 | 78.7173 | 118.1609 | 28.7937 | 22.0953 | 87.2096 | 25.4445 | 136.9643 | 22.0953 | 78.6043 | 28.7937 | 102.6941 | 18.7461 | 75.637 | 18.7461 | 74.4445 | 0 | 0 | 0
Water connection cost | $M | 20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21
MDQ | GJ/day | 22 |  | 0 | 51666.5256 | 0 | 54205.0837 | 0 | 38462.522 | 55344.6133 | 0 | 0 | 36753.4296 | 0 | 48140.7963 | 0 | 38146.3633 | 0 | 51699.114 | 0 | 29846.0569 | 0 | 26510.3528 | 0 | 0 | 0
MDQ cost | $M/year | 23 |  | 0 | 34.3235 | 0 | 36.0099 | 0 | 25.5517 | 36.7669 | 0 | 0 | 24.4163 | 0 | 31.9812 | 0 | 25.3417 | 0 | 34.3451 | 0 | 19.8275 | 0 | 17.6115 | 0 | 0 | 0
24
Capacity credits multiplier - Peak |  | 25 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85714 | 1 | 0.875
Capacity credits multiplier - Flex |  | 26 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0.66667 | 0.66667 | 1 | 1 | 1 | 1 | 0.85714 | 1 | 0.875
27
TUOS |  | 28
- Use of system | $M | 29 |  | 2.6756 | 2.6756 | 2.7272 | 2.7272 | 2.0251 | 2.0256 | 2.9817 | 2.9817 | 2.0709 | 2.0709 | 2.7934 | 2.7935 | 3.0545 | 3.0551 | 3.8368 | 3.8368 | 1.9273 | 1.9273 | 1.7049 | 1.7049 | 1.5684 | 1.5684 | 1.5684
- Control system service price | $M | 30 |  | 0.38009 | 0.38009 | 0.38742 | 0.38742 | 0.28768 | 0.28775 | 0.42358 | 0.42358 | 0.29419 | 0.2942 | 0.39683 | 0.39684 | 0.43392 | 0.434 | 0.54505 | 0.54506 | 0.27378 | 0.27378 | 0.2422 | 0.2422 | 0.2228 | 0.2228 | 0.2228
- Metering charge | $M | 31 |  | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535 | 0.0088535
-Total | $M | 32 |  | 3.0645 | 3.0645 | 3.1235 | 3.1235 | 2.3216 | 2.3222 | 3.4141 | 3.4141 | 2.3739 | 2.374 | 3.1991 | 3.1992 | 3.4973 | 3.4979 | 4.3907 | 4.3907 | 2.2099 | 2.2099 | 1.9559 | 1.9559 | 1.8 | 1.8 | 1.8
33
Working capital |  | 34
- Fuel inventory hours |  | 35 |  | 36 | 14 | 36 | 14 | 36 | 14 | 14 | 36 | 36 | 14 | 36 | 14 | 36 | 14 | 36 | 14 | 36 | 14 | 36 | 14 | 0 | 0 | 0
- Fuel inventory $ |  | 36 |  | 4089368.2491 | 719198.0362 | 4290293.2926 | 754534.765 | 3044183.5745 | 535398.3056 | 770397.0168 | 4380486.2375 | 2908952.3249 | 511607.7404 | 3810255.7856 | 670119.8849 | 3019208.0061 | 530997.3778 | 4091905.7393 | 719651.6667 | 2362293.8814 | 415457.1115 | 2098275.3117 | 369024.1112 | 0 | 0 | 0
- FOM/year (excl WC), $ |  | 37 |  | 11429537.3479 | 45888487.5538 | 11576017.0746 | 47704087.8094 | 9142111.7662 | 34710337.3636 | 51969389.8602 | 15073095.642 | 11299661.9418 | 35817111.7111 | 14143345.5155 | 46323784.8542 | 13705468.0013 | 39429344.3303 | 17161355.8964 | 51637353.8649 | 13049960.4498 | 32953329.5534 | 11655735.342 | 29351465.4109 | 10834953.3811 | 11843653.3178 | 12853128.6129
- Cash cycle $ WC |  | 38 |  | 1408156.5521 | 5653612.4296 | 1426203.3357 | 5877300.3461 | 1126338.2053 | 4276427.6013 | 6402799.5721 | 1857054.9046 | 1392155.4754 | 4412785.8371 | 1742506.6344 | 5707242.4872 | 1688558.686 | 4857824.7635 | 2114335.4287 | 6361891.6466 | 1607798.002 | 4059958.4665 | 1436024.8881 | 3616196.9705 | 1334901.8539 | 1459177.0001 | 1583547.673
- Total WC |  | 39 |  | 5497524.8012 | 6372810.4659 | 5716496.6283 | 6631835.1112 | 4170521.7798 | 4811825.9069 | 7173196.5889 | 6237541.1421 | 4301107.8003 | 4924393.5775 | 5552762.4199 | 6377362.3721 | 4707766.6921 | 5388822.1413 | 6206241.168 | 7081543.3133 | 3970091.8834 | 4475415.578 | 3534300.1999 | 3985221.0818 | 1334901.8539 | 1459177.0001 | 1583547.673
WC annual cost | $M | 40 |  | 0.59648 | 0.69145 | 0.62024 | 0.71955 | 0.4525 | 0.52208 | 0.77829 | 0.67677 | 0.46667 | 0.5343 | 0.60247 | 0.69194 | 0.51079 | 0.58469 | 0.67338 | 0.76835 | 0.43075 | 0.48558 | 0.38347 | 0.4324 | 0.14484 | 0.15832 | 0.17181
41
Bottom of table
Location | Distance from DBNGP, km
Three Springs | 50
Eneabba | 3
Badgingarra | 15
Cataby | 10
Gingin | 10
Muchea | 13
Pinjar | 13
Neerabup | 13
Average | 15.875

## Calculations
Calculations
Configuration |  |  |  | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | CCGT | CCGT | CCGT | CCGT | RECIP | RECIP | RECIP | RECIP | BESS | BESS | BESS
|  |  |  | GT13E2 | GT13E2 | SGT5-2000E | SGT5-2000E | 1x9FA | 1x9FA | LM2500 | LM2500 | LM6000 | LM6000 | LMS100 | LMS100 | 9FA | 9FA | GT13E2 | GT13E2 | Jenbacher | Jenbacher | Wartsila | Wartsila | 6hr | 7hr | 8hr
|  |  |  | DF | GasOnly | DF | GasOnly | DF | GasOnly | GasOnly | DF | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly
Tag |  |  |  | SCGT _GT13E2 _DF | SCGT _GT13E2 _GasOnly | SCGT _SGT5-2000E _DF | SCGT _SGT5-2000E _GasOnly | SCGT _1x9FA _DF | SCGT _1x9FA _GasOnly | SCGT _LM2500 _GasOnly | SCGT _LM2500 _DF | SCGT _LM6000 _DF | SCGT _LM6000 _GasOnly | SCGT _LMS100 _DF | SCGT _LMS100 _GasOnly | CCGT _9FA _DF | CCGT _9FA _GasOnly | CCGT _GT13E2 _DF | CCGT _GT13E2 _GasOnly | RECIP _Jenbacher _DF | RECIP _Jenbacher _GasOnly | RECIP _Wartsila _DF | RECIP _Wartsila _GasOnly | BESS_6hr | BESS_7hr | BESS_8hr
IASR selection |  |  |  | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (large GT) | CCGT | CCGT | CCGT | Gas recip | Gas recip | Gas recip | Gas recip | Battery storage (6hrs storage) | Battery storage (7hrs storage) | Battery storage (8hrs storage)
[24 empty] | 1807.1356 | 2021.8461 | 2237.7778
Configuration net MW (clean-as-new) |  |  |  | 341.1887 | 341.1887 | 347.773 | 347.773 | 258.2408 | 258.3028 | 380.2258 | 380.2258 | 264.0813 | 264.0863 | 356.2173 | 356.2223 | 389.5131 | 389.5811 | 489.2671 | 489.2721 | 245.7632 | 245.7632 | 217.408 | 217.408 | 200 | 200 | 200
# electrical connections |  |  |  | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BESS, $/kW, AUD, $2025
Powerplant cost |  | USD, at notional Vic location, $2025 | EPC+Owners | 330724438.7726 | 323326490.7834 | 329878085.3789 | 322488920.0793 | 278642917.9579 | 256949002.9437 | 599088675.9873 | 613684854.1028 | 503056425.0452 | 493530399.9974 | 549745978.4653 | 538998857.0244 | 574176979.3169 | 550792739.4815 | 687088337.7094 | 679042255.4604 | 376219349.8409 | 366592319.454 | 317597520.999 | 309335228.8412
|  | AUD, at notional Vic location, $2025 | EPC+Owners | 504922807.2864 | 493628230.2037 | 503630664.7006 | 492349496.3042 | 425409035.0502 | 392288554.1125 | 914639199.9806 | 936923441.3783 | 768025076.4049 | 753481526.7136 | 839306837.3516 | 822899018.3578 | 876606075.293 | 840904945.7733 | 1048989828.564 | 1036705733.5274 | 574380686.7799 | 559682930.4641 | 484881711.4488 | 472267524.9484 | 361427119.8466 | 404369222.455 | 447555555.5556
|  | AUD, at notional Vic location, $2026 | EPC+Owners | 521697140.11 | 510027339.3449 | 520362070.5075 | 508706123.8864 | 439541794.8248 | 405320999.2202 | 945024958.2244 | 968049517.3034 | 793540081.9911 | 778513372.6179 | 867189935.5752 | 850237022.9299 | 905728313.0885 | 868841135.6816 | 1083838926.8003 | 1071146734.7326 | 593462520.0195 | 578276481.0342 | 500990247.4281 | 487956997.737 | 373434299.3843 | 417803006.4378 | 462424057.706
|  | AUD, at Average location, $2026 | EPC+Owners | 545132404.9282 | 532938382.6364 | 543737362.3888 | 531557816.5858 | 459286542.4349 | 423528507.4137 | 987476619.2612 | 1011535469.3069 | 829186859.6625 | 813485132.3787 | 906145153.508 | 888430695.5776 | 946414721.4251 | 907870527.4838 | 1132526278.7077 | 1119263938.0631 | 620121572.2685 | 604253358.0942 | 523495333.6499 | 509876614.6616 | 383006598.0608 | 428510878.3114 | 474273611.3784
$ extras
Pre-FID development |  |  |  | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000 | 20000000
Land (PS) |  |  |  | 1442512.5 | 1221577.5 | 1396395 | 1180286.25 | 1311667.5 | 973293.75 | 2064026.25 | 2449590 | 1733696.25 | 1475223.75 | 3056625 | 2587942.5 | 2123550 | 1653795 | 2203987.5 | 1953558.75 | 1645215 | 1313812.5 | 1349741.25 | 1099312.5 | 5550187.5 | 6475218.75 | 7400250
Electrical connection |  |  |  | 41500202 | 41500202 | 41500202 | 41500202 | 26550101 | 26550101 | 41500202 | 41500202 | 26550101 | 26550101 | 41500202 | 41500202 | 26550101 | 26550101 | 41500202 | 41500202 | 26550101 | 26550101 | 26550101 | 26550101 | 26550101 | 26550101 | 26550101
Electrical Fixed Capital Contribution charge |  |  |  | 34118865.9668 | 34118865.9668 | 34777304.0771 | 34777304.0771 | 25824078.3691 | 25830279.541 | 38022583.0078 | 38022583.0078 | 26408129.8828 | 26408630.3711 | 35621731.5674 | 35622232.0557 | 38951309.2041 | 38958108.5205 | 48926708.9844 | 48927209.4727 | 24576321.4111 | 24576321.4111 | 21740798.9502 | 21740798.9502 | 20000000 | 20000000 | 20000000
Gas connection |  |  |  | 28793693.6002 | 102632342.5115 | 28793693.6002 | 95580708.5777 | 22095270.2002 | 78717349.8835 | 118160895.3241 | 28793693.6002 | 22095270.2002 | 87209594.8168 | 25444481.9002 | 136964316.6144 | 22095270.2002 | 78604323.6924 | 28793693.6002 | 102694124.6532 | 18746058.5002 | 75636977.571 | 18746058.5002 | 74444468.7816 | 0 | 0 | 0
Water (external infrastructure) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total extras |  |  |  | 125855274.067 | 199472987.9783 | 126467594.6774 | 193038500.9048 | 95781117.0693 | 152071024.1745 | 219747706.582 | 130766068.6081 | 96787197.333 | 161643549.9379 | 125623040.4676 | 236674693.17 | 109720230.4043 | 165766328.2129 | 141424592.0846 | 215075094.8759 | 91517695.9113 | 148077212.4822 | 88386699.7004 | 143834681.2318 | 72100288.5 | 73025319.75 | 73950351
Total capex incl extras |  |  |  | 670987678.9953 | 732411370.6147 | 670204957.0662 | 724596317.4906 | 555067659.5042 | 575599531.5882 | 1207224325.8432 | 1142301537.915 | 925974056.9955 | 975128682.3166 | 1031768193.9756 | 1125105388.7477 | 1056134951.8294 | 1073636855.6967 | 1273950870.7923 | 1334339032.939 | 711639268.1798 | 752330570.5764 | 611882033.3502 | 653711295.8934 | 455106886.5608 | 501536198.0614 | 548223962.3784
$/kW ($2026) |  |  |  | 1966.6178 | 2146.6463 | 1927.1332 | 2083.5322 | 2149.419 | 2228.3906 | 3175.0192 | 3004.2713 | 3506.3977 | 3692.4622 | 2896.4572 | 3158.436 | 2711.4235 | 2755.8752 | 2603.7943 | 2727.1922 | 2895.6297 | 3061.2009 | 2814.4413 | 3006.8412 | 2275.5344 | 2507.681 | 2741.1198
Annualised capex | $/year |  |  | 92539681.058 | 101010967.5061 | 92431731.4787 | 99933149.6173 | 76552499.821 | 79384165.6677 | 166495090.113 | 157541223.6318 | 127706285.2044 | 134485475.7799 | 142296949.0875 | 155169606.0758 | 145657505.5788 | 148071291.4835 | 175697722.8602 | 184026193.6201 | 98146170.1418 | 103758136.2978 | 84388089.3553 | 90156997.9893 | 62766347.9495 | 69169675.1827 | 75608647.0959
| $/MW/y |  |  | 271227.3062 | 296056.0518 | 265781.7618 | 287351.6285 | 296438.4584 | 307329.8744 | 437884.7436 | 414335.9319 | 483587.0081 | 509248.2037 | 399466.6818 | 435597.651 | 373947.6504 | 380078.2356 | 359103.9056 | 376122.3982 | 399352.5658 | 422187.4159 | 388155.4194 | 414690.3626 | 313831.7397 | 345848.3759 | 378043.2355
"Weighted average cost of capital" factor | $/MW/y |  |  | 14335.249 | 15647.5293 | 14047.4342 | 15187.4721 | 15667.7407 | 16243.3876 | 23143.6389 | 21899.0073 | 25559.1528 | 26915.4308 | 21113.1188 | 23022.7586 | 19764.3547 | 20088.3761 | 18979.8143 | 19879.2972 | 21107.0874 | 22313.9839 | 20515.2817 | 21917.7401 | 16587.0325 | 18279.2163 | 19980.8197
FOM, $/MW/y
Plant FOM, Technology IASR |  |  |  | 14323.4078 | 14323.4078 | 14323.4078 | 14323.4078 | 14323.4078 | 14323.4078 | 17685.8344 | 17685.8344 | 17685.8344 | 17685.8344 | 17685.8344 | 17685.8344 | 14323.4078 | 15303.0124 | 15303.0124 | 15303.0124 | 29400 | 29400 | 29400 | 29400 | 29785.275 | 33883.9325 | 37982.59
Transmission connection asset maintenance |  |  |  | 608.1709 | 608.1709 | 596.6564 | 596.6564 | 514.0571 | 513.9337 | 545.731 | 545.731 | 502.688 | 502.6785 | 582.5124 | 582.5042 | 340.8114 | 340.7519 | 424.1058 | 424.1015 | 540.1561 | 540.1561 | 610.6055 | 610.6055 | 663.7525 | 663.7525 | 663.7525
Transmission NUOS |  |  |  | 8981.879 | 8981.879 | 8981.3877 | 8981.3877 | 8990.2139 | 8990.2057 | 8979.2149 | 8979.2149 | 8989.4557 | 8989.4551 | 8980.7842 | 8980.7839 | 8978.6597 | 8978.6557 | 8974.0254 | 8974.0253 | 8991.9545 | 8991.9545 | 8996.653 | 8996.653 | 9000.1975 | 9000.1975 | 9000.1975
DBNGP capacity |  |  |  | 0 | 100599.663 | 0 | 103544.2443 | 0 | 98921.4576 | 96697.578 | 0 | 0 | 92455.7337 | 0 | 89778.8416 | 0 | 65048.4772 | 0 | 70196.3466 | 0 | 80677.4086 | 0 | 81006.8722 | 0 | 0 | 0
Gas connection FOM |  |  |  | 210.9807 | 752.0205 | 206.9862 | 687.0911 | 213.9018 | 761.8709 | 776.9126 | 189.3197 | 209.1711 | 825.5785 | 178.5742 | 961.2278 | 141.8134 | 504.4157 | 147.1267 | 524.7291 | 190.6923 | 769.4091 | 215.5631 | 856.0457 | 0 | 0 | 0
Working capital |  |  |  | 1748.2452 | 2026.5912 | 1783.4617 | 2069.0336 | 1752.2469 | 2021.2058 | 2046.9199 | 1779.9244 | 1767.1459 | 2023.1898 | 1691.3123 | 1942.4494 | 1311.362 | 1500.81 | 1376.2977 | 1570.3889 | 1752.7235 | 1975.8148 | 1763.8339 | 1988.8712 | 724.1843 | 791.6035 | 859.0746
Corporate overheads etc |  |  |  | 3847.9444 | 3847.9444 | 3775.0914 | 3775.0914 | 5083.9181 | 5082.6976 | 3452.8822 | 3452.8822 | 4971.4804 | 4971.3862 | 3685.6013 | 3685.5495 | 3370.5542 | 3369.966 | 2683.3503 | 2683.3229 | 5342.0322 | 5342.0322 | 6038.7615 | 6038.7615 | 6564.375 | 6564.375 | 6564.375
Insurance adjustment |  |  |  | 4793.2344 | 4686.0149 | 4690.4501 | 4585.3855 | 5335.5617 | 4918.977 | 7791.2378 | 7981.0633 | 9419.6772 | 9241.1282 | 7631.3962 | 7482.103 | 7289.2137 | 6991.1289 | 6944.2211 | 6862.8312 | 7569.7444 | 7376.0432 | 7223.6812 | 7035.7573 | 5745.099 | 6427.6632 | 7114.1042
Site security |  |  |  | 493.803 | 493.803 | 484.4539 | 484.4539 | 652.4144 | 652.2577 | 443.1051 | 443.1051 | 637.9854 | 637.9733 | 472.9697 | 472.9631 | 432.54 | 432.4645 | 344.3518 | 344.3483 | 685.5379 | 685.5379 | 774.9485 | 774.9485 | 842.4 | 842.4 | 842.4
Rates |  |  |  | 239.751 | 203.0308 | 227.692 | 192.454 | 288.0278 | 213.6733 | 307.8286 | 365.3316 | 372.2809 | 316.7725 | 486.5893 | 411.9732 | 309.1547 | 240.7239 | 255.4457 | 226.4183 | 379.6131 | 303.1461 | 352.0549 | 286.7353 | 1573.6679 | 1835.9459 | 2098.2238
Total |  |  |  | 35247.4165 | 136522.5255 | 35069.5871 | 139239.2056 | 37153.7495 | 136399.6871 | 138727.2445 | 41422.4064 | 44555.719 | 137649.73 | 41395.574 | 131984.23 | 36497.517 | 102710.4063 | 36451.9369 | 107109.5243 | 54852.4541 | 136061.5024 | 55376.1016 | 136995.2501 | 54898.9512 | 60009.8701 | 65124.7177
Total annual costs | $/MW/y | $2026 |  | 320809.9717 | 448226.1066 | 314898.7831 | 441778.3062 | 349259.9486 | 459972.9491 | 599755.627 | 477657.3456 | 553701.88 | 673813.3646 | 461975.3746 | 590604.6396 | 430209.5221 | 502877.018 | 414535.6568 | 503111.2197 | 475312.1074 | 580562.9022 | 464046.8027 | 573603.3528 | 385317.7234 | 424137.4623 | 463148.7729
- escalate to $2029 | $/MW/y |  |  | 351366.7637 | 490919.1434 | 344892.541 | 483857.1972 | 382526.5692 | 503784.8596 | 656881.6816 | 523153.675 | 606441.3665 | 737993.3361 | 505978.0138 | 646859.0728 | 471186.4993 | 550775.4931 | 454019.7158 | 551032.0022 | 520585.0555 | 635860.8711 | 508246.7432 | 628238.4324 | 422018.8068 | 464536.0825 | 507263.177
|  |  |  | SCGT _GT13E2 _DF | SCGT _GT13E2 _GasOnly | SCGT _SGT5-2000E _DF | SCGT _SGT5-2000E _GasOnly | SCGT _1x9FA _DF | SCGT _1x9FA _GasOnly | SCGT _LM2500 _GasOnly | SCGT _LM2500 _DF | SCGT _LM6000 _DF | SCGT _LM6000 _GasOnly | SCGT _LMS100 _DF | SCGT _LMS100 _GasOnly | CCGT _9FA _DF | CCGT _9FA _GasOnly | CCGT _GT13E2 _DF | CCGT _GT13E2 _GasOnly | RECIP _Jenbacher _DF | RECIP _Jenbacher _GasOnly | RECIP _Wartsila _DF | RECIP _Wartsila _GasOnly | BESS_6hr | BESS_7hr | BESS_8hr
Proxy BRCP - Peak |  | $2029 |  | 351366.7637 | 490919.1434 | 344892.541 | 483857.1972 | 382526.5692 | 503784.8596 | 656881.6816 | 523153.675 | 606441.3665 | 737993.3361 | 505978.0138 | 646859.0728 | 0 | 0 | 454019.7158 | 551032.0022 | 520585.0555 | 635860.8711 | 508246.7432 | 628238.4324 | 492355.2746 | 464536.0825 | 579729.3451
Proxy BRCP - Flex |  | $2029 |  | 351366.7637 | 490919.1434 | 344892.541 | 483857.1972 | 382526.5692 | 503784.8596 | 656881.6816 | 523153.675 | 606441.3665 | 737993.3361 | 505978.0138 | 646859.0728 | 0 | 0 | 681029.5737 | 826548.0034 | 520585.0555 | 635860.8711 | 508246.7432 | 628238.4324 | 492355.2746 | 464536.0825 | 579729.3451

## WP
Values adopted:
|  | # connections | $M
|  | 1 | 26550101
|  | 2 | 41500202
WesternPower
Single connection:
Double connection:
Add CB, isolator and gantry landing to the breaker-and-half arrangement shown (assume 1.5M), add second tx line and easement value
WesternPower tariffs |  |  | 2026-27 Price List for the Western Power Network Proposed by Western Power on 31 March 2026
Reference tariffs RT11, TRT2 and TRT3 |  |  | https://www.erawa.com.au/sites/default/files/2026-27-price-list-for-the-western-power-network.PDF
Substation | TNI | Use of System Price (c/kW/day)
Albany | WALB | 3.093
Alcoa Pinjarra | WAPJ | 2.749
Badgingarra | WBGA | 3.153
Bluewaters | WBWP | 3.112
Boulder | WBLD | 2.239
Cockburn PWS | WCKB | 1.887 |  | Values for TUOS charge calculation:
Collgar | WCGW | 3.571 |  |  | Use of System Price (c/kW/day) | Follows GHD report for ERA 2028/29 Table 19 but using updated WP pricing
Collie PWS | WCPS | 3.619 |  | Badgingarra | 3.153
Cunderdin Solar Farm | WCSF | 2.599 |  | Pinjar GTS | 1.569
Emu Downs | WEMD | 3.153 |  | Newgen Neerabup | 1.933
Geraldton | WGTN | 0.529 |  | Yandin Wind Farm | 1.933
Greenough Solar Farm | TMSG | 0.674 |  | Average | 2.147
Kemerton PWS | WKEM | 2.515
Kwinana Alcoa | WAKW | 1.946
Kwinana BESS | WKWB | 1.887
Kwinana Donaldson Road | WKND | 1.479
Kwinana PWS | WKPS | 1.887
Kwinana Waste to Energy | WKWW | 1.479
Landwehr (Alinta) | WLWT | 2.347
Mason Road | WNSF | 1.479
Merredin Power Station | TMDP | 2.599
Merredin Solar Farm | WMSF | 2.599
Muja PWS | WMPS | 3.798
Mumbida Wind Farm | TMMB | 3.2
Mungarra GTS | WMGA | 3.144
Neerabup BESS | WPMB | 3.619
Newgen Kwinana | WNGK | 2.195
Newgen Neerabup | WGNN | 1.933
Oakey (Alinta) | WOLY | 2.617
Parkeston | WPKS | 2.699
Pinjar GTS | WPJR | 1.569
Synergy Collie BESS | WCBB | 3.619
TiWest GT | WKMN | 1.524
Wagerup | WWGP | 2.164
Walkaway Windfarm | WWWF | 3.471
Warradarge Wind Farm | WWDW | 3.153
West Kalgoorlie GT | WWKT | 2.195
Worsley | WWDL | 2.457
Yandin Wind Farm | WYDW | 1.933
Control System Service Price (Generators) | cents/kW/day
Control system service price (Generators) | 0.305
Metering price | cents/meter/day
TRT1, TRT2 and TRT3 | 1211.979

## Gas
Parameters
Cost ref date: |  | 2024-06-30
Esc 2024 to 2026 |  | 1.0549
Compressors |  | 4.7 | $M/MW | GHD for AEMO Jun24
|  | 4.9579 | $2026
Pipe |  | 100000 | $/in/km | GHD for AEMO Jun24
|  | 105486.9827 | $2026
Land |  | 0.53625 | $M/Ha | Compressor station land. Pipeline easement cost not calculated. Gas receival station included in powerplant land
| Area: | 5 | Ha | For gas compressor station aat top of lateral
Pipeline distance |  | 15.875 | km
Fat lateral case (for gas only configs)
Storage hours |  | 14 | hours |  |  | Storage is the length of a 36 inch pipe needed to contain the required fuel for a run, between the two pressure ranges
Recharge hours |  | 24 | hours
Allowance for facilities |  | 2 | $M |  |  | A nominal allowance
Min lateral pressure higher than engine/GT pressure |  | 5 | Bar
[10 empty] | 11 | [7 empty] | 20
Configuration | [9 empty] | Compressor |  |  | Lateral | Cost, $M
| Net MW | LHV HR | HHV HR | GJ/h | kg/s | GJ for 14 hours |  | kg/s recharge | Power, MW | MDQ | GT/Engine P ratio | Pmin Mpa | km | Compressors | Pipe | Facilities | Comp land | Total | $/kW
SCGT _GT13E2 _GasOnly | 341.1887 | 9771 | 10816.497 | 3690.4661 | 20.5026 | 51666.5256 |  | 11.9598 | 3.7255 | 51666.5256 | 26.6 | 3.2019 | 20.9295 | 18.4707 | 79.4804 | 2 | 2.6812 | 102.6323 | 300.8082
SCGT _SGT5-2000E _GasOnly | 347.773 | 10057 | 11133.099 | 3871.7917 | 21.51 | 54205.0837 |  | 12.5475 | 3.9086 | 54205.0837 | 20.75 | 2.6091 | 18.8336 | 19.3782 | 71.5212 | 2 | 2.6812 | 95.5807 | 274.8365
SCGT _1x9FA _GasOnly | 258.3028 | 9608 | 10636.056 | 2747.323 | 15.2629 | 38462.522 |  | 8.9034 | 2.7734 | 38462.522 | 28.37 | 3.3812 | 15.875 | 13.7503 | 60.2858 | 2 | 2.6812 | 78.7173 | 304.7483
SCGT _LM2500 _GasOnly | 380.2258 | 9392 | 10396.944 | 3953.1867 | 21.9621 | 55344.6133 |  | 12.8113 | 3.9907 | 55344.6133 | 37.61 | 4.3175 | 24.6724 | 19.7856 | 93.694 | 2 | 2.6812 | 118.1609 | 310.765
SCGT _LM6000 _GasOnly | 264.0863 | 8980 | 9940.86 | 2625.245 | 14.5847 | 36753.4296 |  | 8.5077 | 2.6502 | 36753.4296 | 50.91 | 5.6651 | 18.2721 | 13.1393 | 69.3891 | 2 | 2.6812 | 87.2096 | 330.2314
SCGT _LMS100 _GasOnly | 356.2223 | 8720 | 9653.04 | 3438.6283 | 19.1035 | 48140.7963 |  | 11.1437 | 3.4713 | 48140.7963 | 60.21 | 6.6074 | 30.302 | 17.2103 | 115.0728 | 2 | 2.6812 | 136.9643 | 384.4911
CCGT _9FA _GasOnly | 389.5811 | 6318 | 6994.026 | 2724.7402 | 15.1374 | 38146.3633 |  | 8.8302 | 2.7506 | 38146.3633 | 28.37 | 3.3812 | 15.875 | 13.6373 | 60.2858 | 2 | 2.6812 | 78.6043 | 201.7663
CCGT _GT13E2 _GasOnly | 489.2721 | 6818 | 7547.526 | 3692.7939 | 20.5155 | 51699.114 |  | 11.9674 | 3.7279 | 51699.114 | 26.6 | 3.2019 | 20.9427 | 18.4823 | 79.5305 | 2 | 2.6812 | 102.6941 | 209.8916
RECIP _Jenbacher _GasOnly | 245.7632 | 7836 | 8674.452 | 2131.8612 | 11.8437 | 29846.0569 |  | 6.9088 | 2.1521 | 29846.0569 | 11.35 | 1.6567 | 15.875 | 10.6699 | 60.2858 | 2 | 2.6812 | 75.637 | 307.7636
RECIP _Wartsila _GasOnly | 217.408 | 7868 | 8709.876 | 1893.5966 | 10.52 | 26510.3528 |  | 6.1367 | 1.9116 | 26510.3528 | 6.993 | 1.2152 | 15.875 | 9.4774 | 60.2858 | 2 | 2.6812 | 74.4445 | 342.4183
Skinny lateral case (for DF configs)
Config as above except no compressor station needed. Length is the pipeline distance and diameter simply based on typical flow velocity
Flow velocity | 7 | m/s
Reference pressure (typ) | 5 | MPa | DBNGP is MAOP 8.48 Mpag
Cost, $M
Configuration | Net MW | LHV HR | HHV HR | GJ/h | kg/s | m3/s | Dia theor, mm | Dia inches |  | MDQ |  |  | km | Compressors | Pipe | Facilities | Comp land | Total | $/kW
SCGT _GT13E2 _DF | 341.1887 | 9771 | 10816.497 | 3690.4661 | 20.5026 | 0.57812 | 324.2774 | 16 |  | 0 |  |  | 15.875 | 0 | 26.7937 | 2 | 0 | 28.7937 | 84.3923
SCGT _SGT5-2000E _DF | 347.773 | 10057 | 11133.099 | 3871.7917 | 21.51 | 0.60653 | 332.1484 | 16 |  | 0 |  |  | 15.875 | 0 | 26.7937 | 2 | 0 | 28.7937 | 82.7945
SCGT _1x9FA _DF | 258.2408 | 9610 | 10638.27 | 2747.2352 | 15.2624 | 0.43036 | 279.7847 | 12 |  | 0 |  |  | 15.875 | 0 | 20.0953 | 2 | 0 | 22.0953 | 85.5607
SCGT _LM2500 _DF | 380.2258 | 9392 | 10396.944 | 3953.1867 | 21.9621 | 0.61928 | 335.6215 | 16 |  | 0 |  |  | 15.875 | 0 | 26.7937 | 2 | 0 | 28.7937 | 75.7279
SCGT _LM6000 _DF | 264.0813 | 8980 | 9940.86 | 2625.1952 | 14.5844 | 0.41125 | 273.4997 | 12 |  | 0 |  |  | 15.875 | 0 | 20.0953 | 2 | 0 | 22.0953 | 83.6684
SCGT _LMS100 _DF | 356.2173 | 8720 | 9653.04 | 3438.58 | 19.1032 | 0.53867 | 313.0154 | 14 |  | 0 |  |  | 15.875 | 0 | 23.4445 | 2 | 0 | 25.4445 | 71.4297
CCGT _9FA _DF | 389.5131 | 6319 | 6995.133 | 2724.6959 | 15.1372 | 0.42683 | 278.6347 | 12 |  | 0 |  |  | 15.875 | 0 | 20.0953 | 2 | 0 | 22.0953 | 56.7254
CCGT _GT13E2 _DF | 489.2671 | 6818 | 7547.526 | 3692.7561 | 20.5153 | 0.57848 | 324.378 | 16 |  | 0 |  |  | 15.875 | 0 | 26.7937 | 2 | 0 | 28.7937 | 58.8507
RECIP _Jenbacher _DF | 245.7632 | 7836 | 8674.452 | 2131.8612 | 11.8437 | 0.33396 | 246.4652 | 10 |  | 0 |  |  | 15.875 | 0 | 16.7461 | 2 | 0 | 18.7461 | 76.2769
RECIP _Wartsila _DF | 217.408 | 7868 | 8709.876 | 1893.5966 | 10.52 | 0.29664 | 232.2843 | 10 |  | 0 |  |  | 15.875 | 0 | 16.7461 | 2 | 0 | 18.7461 | 86.2253
In DF cases the RCP is certified on distillate. That the plant might elsewise run on gas does not charge MDQ against the RCP function. That is assumed from Portfolio gas the generator may have. MDQ=0 for RCP
DBNGP tariff | [8 empty] | https://www.erawa.com.au/access/gas-access/dampier-to-bunbury-natural-gas-pipeline/tariff-variations
$/GJ/day
DBNGP tariff | 1.8188
Gas cost for WC calc
Working capital is minor factor. Only an approximate cost is necessary
Assumed gas cost | 13.92 | $/GJ | EPWA non-residential pricing 2026-27. Will over-estimate costs to a power generator, but adopted
https://www.wa.gov.au/organisation/energy-policy-wa/business-and-government-gas-pricing
Factors used in calcs
HHV/LHV | 1.107
GJ/tonne | 50
Gas commpressor |  | One stage
| k | 1.31
| Tin | 41 | C | 314.15
| P2 | 13 | MPa | MAOP - a margin
| P1 | 3 | MPa
| P2/P1 | 4.2244
| T2/T1 | 1.4063
| T2 | 168.6437 |  | 441.7937
| M | 3.6 |  | t/h
| Pis | 280.352 | kW | per (kg/s)
| effic | 90%
| Pis | 311.5022 | kW | per (kg/s)
Natural gas at 41C
P | Z | Density
Mpa |  | kg/m3
13 | 0.8478 | 99.417
6 | 0.875 | 48.905
5 | 0.9254 | 35.464
4 | 0.9391 | 28.096
3 | 0.9533 | 20.929
1 | 0.9767 | 7.909
Pipe | 36 | inch
| 894.94 | mm ID
| 0.62904 | m2
| 629.0387 | m3/km
Storage/km
| Mpa LP from 13 Mpa | kg/km | GJ/km
| 1 | 57562.0719 | 2878.1036
| 3 | 49371.9882 | 2468.5994
| 4 | 44863.668 | 2243.1834
| 5 | 40228.9109 | 2011.4455
| 6 | 31774.002 | 1588.7001
Skinny pipe diameters
| Nominal Size (NPS), in | Outside Diameter (mm) | Approximate Internal Diameter (mm) | Nominal Size (NPS), in
| 8 | 219.1 | 194 | 8
| 10 | 273.1 | 247 | 10
| 12 | 323.9 | 295 | 12
| 14 | 355.6 | 324 | 14
| 16 | 406.4 | 371 | 16
DBNGP
Power station
Facilities
Storage lateral
Compressor station duty/standby

## Distillate
Data for LOCATION: PERTH
Time is native time for database (UTC+0)
Terminal Gate Price for Automotive Distillate in Australia, AUD cents per litre including GST
Citation: Shell Australia and Viva Energy website, ad-hoc times
| PRICE c/L | Excise | Less GST and excise
2025-01-07 | 171.69 | 50 | 106.0818 | Average | 99.3043 | c/L
2025-01-13 | 172.49 | 50 | 106.8091 | Add allowance for transport etc | 20 | c/L | Transport to PS plus margin
2025-01-26 | 179.14 | 50 | 112.8545 | Delivered cost | 119.3043 | c/L
2025-02-08 | 172.3 | 50.8 | 105.8364 | Density | 0.85 | kg/L
2025-02-16 | 170.95 | 50.8 | 104.6091 | HHV | 45.6 | GJ/t
2025-03-02 | 169.05 | 50.8 | 102.8818 | Cost | 30.7803 | $/GJ
2025-03-07 | 166.86 | 50.8 | 100.8909
2025-03-22 | 163.06 | 50.8 | 97.4364
2025-04-18 | 157.38 | 50.8 | 92.2727
2025-04-28 | 158.15 | 50.8 | 92.9727
2025-05-24 | 156.65 | 50.8 | 91.6091
2025-06-06 | 155.79 | 50.8 | 90.8273
2025-06-17 | 159.43 | 50.8 | 94.1364
2025-07-05 | 162.98 | 50.8 | 97.3636
2025-08-04 | 169.22 | 51.6 | 102.2364
2025-08-22 | 161.38 | 51.6 | 95.1091
2025-09-02 | 163.43 | 51.6 | 96.9727
2025-09-19 | 164.33 | 51.6 | 97.7909
2025-09-26 | 163.89 | 51.6 | 97.3909
2025-10-31 | 169.28 | 51.6 | 102.2909
2025-11-24 | 174.98 | 51.6 | 107.4727
2025-12-04 | 164.7 | 51.6 | 98.1273
2025-12-24 | 155.79 | 51.6 | 90.0273

## CPI_FX
Sources:
| Historical CPI | RBA | https://www.rba.gov.au/statistics/tables/xls/g01hist.xlsx?v=2026-07-22-16-00-57
Projected CPI
| Historical fx | RBA | https://www.rba.gov.au/statistics/tables/xls-hist/2023-current.xls?v=2026-07-02-11-27-20
F11.1 EXCHANGE RATES |  |  |  | G1 CONSUMER PRICE INFLATION |  |  |  | Index
Title | A$1=USD |  |  | Title | Consumer price index | 2025-12-31 | 3.6% | 100.32
Description | AUD/USD Exchange Rate; see notes for further detail. |  |  | Description | Consumer price index; All groups | 2026-06-30 | 4.8% | 102.7277
Frequency | Daily |  |  | Frequency | Quarterly | 2026-12-31 | 4% | 104.7822
Type | Indicative |  |  | Type | Original | 2027-06-30 | 2.4% | 106.0396
Units | USD |  |  | Units | Index, September 2025 month = 100 | 2027-12-31 | 2.4% | 107.3121
[6 empty] | 2028-06-30 | 2.5% | 108.6535
[6 empty] | 2028-12-31 | 2.5% | 110.0117 | Assume mid range of target band
Source | WM/Reuters |  |  | Source | ABS / RBA | 2029-06-30 | 2.5% | 111.3868 | Assume mid range of target band
Publication date | 2026-07-21 |  |  | Publication date | 30-Apr-2026 | 2029-12-31 | 2.5% | 112.7791 | Assume mid range of target band
Series ID | FXRUSD |  |  | Series ID | GCPIAG
2023-01-03 | 0.6828 |  |  | 1922-06-30 | 1.93
2023-01-04 | 0.6809 |  |  | 1922-09-30 | 1.93
2023-01-05 | 0.6815 |  |  | 1922-12-31 | 1.91
2023-01-06 | 0.6769 |  |  | 1923-03-31 | 1.92
2023-01-09 | 0.6929 |  |  | 1923-06-30 | 1.98
2023-01-10 | 0.6904 |  |  | 1923-09-30 | 2
2023-01-11 | 0.6911 |  |  | 1923-12-31 | 2
2023-01-12 | 0.6923 |  |  | 1924-03-31 | 1.94
2023-01-13 | 0.6955 |  |  | 1924-06-30 | 1.94
2023-01-16 | 0.6988 |  |  | 1924-09-30 | 1.93
2023-01-17 | 0.6973 |  |  | 1924-12-31 | 1.93
2023-01-18 | 0.6994 |  |  | 1925-03-31 | 1.96
2023-01-19 | 0.6904 |  |  | 1925-06-30 | 1.98
2023-01-20 | 0.6918 |  |  | 1925-09-30 | 1.99
2023-01-23 | 0.6983 |  |  | 1925-12-31 | 1.98
2023-01-24 | 0.7033 |  |  | 1926-03-31 | 1.99
2023-01-25 | 0.7102 |  |  | 1926-06-30 | 2.03
2023-01-27 | 0.7107 |  |  | 1926-09-30 | 2
2023-01-30 | 0.7092 |  |  | 1926-12-31 | 1.99
2023-01-31 | 0.7037 |  |  | 1927-03-31 | 1.98
2023-02-01 | 0.7068 |  |  | 1927-06-30 | 1.97
2023-02-02 | 0.715 |  |  | 1927-09-30 | 1.99
2023-02-03 | 0.7062 |  |  | 1927-12-31 | 2
2023-02-06 | 0.6943 |  |  | 1928-03-31 | 2
2023-02-07 | 0.6931 |  |  | 1928-06-30 | 2.01
2023-02-08 | 0.6964 |  |  | 1928-09-30 | 2
2023-02-09 | 0.6954 |  |  | 1928-12-31 | 2
2023-02-10 | 0.6923 |  |  | 1929-03-31 | 2.05
2023-02-13 | 0.6908 |  |  | 1929-06-30 | 2.05
2023-02-14 | 0.6975 |  |  | 1929-09-30 | 2.05
2023-02-15 | 0.6937 |  |  | 1929-12-31 | 2.05
2023-02-16 | 0.6922 |  |  | 1930-03-31 | 1.99
2023-02-17 | 0.6843 |  |  | 1930-06-30 | 1.97
2023-02-20 | 0.6892 |  |  | 1930-09-30 | 1.91
2023-02-21 | 0.6896 |  |  | 1930-12-31 | 1.84
2023-02-22 | 0.6839 |  |  | 1931-03-31 | 1.79
2023-02-23 | 0.683 |  |  | 1931-06-30 | 1.74
2023-02-24 | 0.6814 |  |  | 1931-09-30 | 1.69
2023-02-27 | 0.6711 |  |  | 1931-12-31 | 1.67
2023-02-28 | 0.673 |  |  | 1932-03-31 | 1.67
2023-03-01 | 0.675 |  |  | 1932-06-30 | 1.65
2023-03-02 | 0.6746 |  |  | 1932-09-30 | 1.63
2023-03-03 | 0.6744 |  |  | 1932-12-31 | 1.6
2023-03-06 | 0.6756 |  |  | 1933-03-31 | 1.58
2023-03-07 | 0.6713 |  |  | 1933-06-30 | 1.59
2023-03-08 | 0.6591 |  |  | 1933-09-30 | 1.59
2023-03-09 | 0.661 |  |  | 1933-12-31 | 1.59
2023-03-10 | 0.6599 |  |  | 1934-03-31 | 1.6
2023-03-13 | 0.6665 |  |  | 1934-06-30 | 1.62
2023-03-14 | 0.6649 |  |  | 1934-09-30 | 1.62
2023-03-15 | 0.6692 |  |  | 1934-12-31 | 1.62
2023-03-16 | 0.6637 |  |  | 1935-03-31 | 1.63
2023-03-17 | 0.6714 |  |  | 1935-06-30 | 1.63
2023-03-20 | 0.6683 |  |  | 1935-09-30 | 1.65
2023-03-21 | 0.6691 |  |  | 1935-12-31 | 1.66
2023-03-22 | 0.6695 |  |  | 1936-03-31 | 1.66
2023-03-23 | 0.6741 |  |  | 1936-06-30 | 1.66
2023-03-24 | 0.6687 |  |  | 1936-09-30 | 1.69
2023-03-27 | 0.665 |  |  | 1936-12-31 | 1.7
2023-03-28 | 0.6689 |  |  | 1937-03-31 | 1.71
2023-03-29 | 0.6703 |  |  | 1937-06-30 | 1.71
2023-03-30 | 0.6687 |  |  | 1937-09-30 | 1.73
2023-03-31 | 0.6712 |  |  | 1937-12-31 | 1.74
2023-04-03 | 0.6663 |  |  | 1938-03-31 | 1.75
2023-04-04 | 0.6765 |  |  | 1938-06-30 | 1.77
2023-04-05 | 0.6736 |  |  | 1938-09-30 | 1.79
2023-04-06 | 0.6694 |  |  | 1938-12-31 | 1.79
2023-04-11 | 0.6677 |  |  | 1939-03-31 | 1.82
2023-04-12 | 0.6671 |  |  | 1939-06-30 | 1.81
2023-04-13 | 0.6701 |  |  | 1939-09-30 | 1.81
2023-04-14 | 0.6783 |  |  | 1939-12-31 | 1.83
2023-04-17 | 0.6715 |  |  | 1940-03-31 | 1.84
2023-04-18 | 0.6733 |  |  | 1940-06-30 | 1.88
2023-04-19 | 0.6727 |  |  | 1940-09-30 | 1.89
2023-04-20 | 0.6715 |  |  | 1940-12-31 | 1.95
2023-04-21 | 0.6708 |  |  | 1941-03-31 | 1.97
2023-04-24 | 0.6676 |  |  | 1941-06-30 | 1.98
2023-04-26 | 0.6609 |  |  | 1941-09-30 | 1.99
2023-04-27 | 0.6627 |  |  | 1941-12-31 | 2.03
2023-04-28 | 0.661 |  |  | 1942-03-31 | 2.08
2023-05-01 | 0.6639 |  |  | 1942-06-30 | 2.14
2023-05-02 | 0.6705 |  |  | 1942-09-30 | 2.19
2023-05-03 | 0.6664 |  |  | 1942-12-31 | 2.22
2023-05-04 | 0.669 |  |  | 1943-03-31 | 2.22
2023-05-05 | 0.6735 |  |  | 1943-06-30 | 2.26
2023-05-08 | 0.6775 |  |  | 1943-09-30 | 2.24
2023-05-09 | 0.6778 |  |  | 1943-12-31 | 2.22
2023-05-10 | 0.6764 |  |  | 1944-03-31 | 2.22
2023-05-11 | 0.6775 |  |  | 1944-06-30 | 2.22
2023-05-12 | 0.669 |  |  | 1944-09-30 | 2.23
2023-05-15 | 0.6682 |  |  | 1944-12-31 | 2.22
2023-05-16 | 0.6674 |  |  | 1945-03-31 | 2.22
2023-05-17 | 0.6639 |  |  | 1945-06-30 | 2.22
2023-05-18 | 0.6647 |  |  | 1945-09-30 | 2.22
2023-05-19 | 0.6634 |  |  | 1945-12-31 | 2.23
2023-05-22 | 0.664 |  |  | 1946-03-31 | 2.24
2023-05-23 | 0.665 |  |  | 1946-06-30 | 2.26
2023-05-24 | 0.6598 |  |  | 1946-09-30 | 2.26
2023-05-25 | 0.6527 |  |  | 1946-12-31 | 2.28
2023-05-26 | 0.6515 |  |  | 1947-03-31 | 2.3
2023-05-29 | 0.6547 |  |  | 1947-06-30 | 2.32
2023-05-30 | 0.6509 |  |  | 1947-09-30 | 2.35
2023-05-31 | 0.6495 |  |  | 1947-12-31 | 2.41
2023-06-01 | 0.6511 |  |  | 1948-03-31 | 2.47
2023-06-02 | 0.6612 |  |  | 1948-06-30 | 2.52
2023-06-05 | 0.6607 |  |  | 1948-09-30 | 2.59
2023-06-06 | 0.6661 |  |  | 1948-12-31 | 2.63
2023-06-07 | 0.6678 |  |  | 1949-03-31 | 2.71
2023-06-08 | 0.6662 |  |  | 1949-06-30 | 2.74
2023-06-09 | 0.6708 |  |  | 1949-09-30 | 2.82
2023-06-13 | 0.6761 |  |  | 1949-12-31 | 2.86
2023-06-14 | 0.6767 |  |  | 1950-03-31 | 2.9
2023-06-15 | 0.6821 |  |  | 1950-06-30 | 3.02
2023-06-16 | 0.6888 |  |  | 1950-09-30 | 3.05
2023-06-19 | 0.6865 |  |  | 1950-12-31 | 3.17
2023-06-20 | 0.6803 |  |  | 1951-03-31 | 3.32
2023-06-21 | 0.6783 |  |  | 1951-06-30 | 3.52
2023-06-22 | 0.6765 |  |  | 1951-09-30 | 3.71
2023-06-23 | 0.6697 |  |  | 1951-12-31 | 3.98
2023-06-26 | 0.6679 |  |  | 1952-03-31 | 4.1
2023-06-27 | 0.6712 |  |  | 1952-06-30 | 4.25
2023-06-28 | 0.6646 |  |  | 1952-09-30 | 4.33
2023-06-29 | 0.6614 |  |  | 1952-12-31 | 4.37
2023-06-30 | 0.663 |  |  | 1953-03-31 | 4.41
2023-07-03 | 0.6664 |  |  | 1953-06-30 | 4.45
2023-07-04 | 0.6653 |  |  | 1953-09-30 | 4.48
2023-07-05 | 0.6688 |  |  | 1953-12-31 | 4.45
2023-07-06 | 0.6661 |  |  | 1954-03-31 | 4.48
2023-07-07 | 0.6635 |  |  | 1954-06-30 | 4.48
2023-07-10 | 0.6657 |  |  | 1954-09-30 | 4.48
2023-07-11 | 0.6682 |  |  | 1954-12-31 | 4.48
2023-07-12 | 0.6709 |  |  | 1955-03-31 | 4.52
2023-07-13 | 0.6808 |  |  | 1955-06-30 | 4.56
2023-07-14 | 0.6889 |  |  | 1955-09-30 | 4.6
2023-07-17 | 0.6814 |  |  | 1955-12-31 | 4.64
2023-07-18 | 0.6821 |  |  | 1956-03-31 | 4.68
2023-07-19 | 0.6794 |  |  | 1956-06-30 | 4.83
2023-07-20 | 0.6828 |  |  | 1956-09-30 | 4.95
2023-07-21 | 0.6775 |  |  | 1956-12-31 | 4.95
2023-07-24 | 0.6736 |  |  | 1957-03-31 | 4.95
2023-07-25 | 0.6768 |  |  | 1957-06-30 | 4.99
2023-07-26 | 0.6763 |  |  | 1957-09-30 | 4.99
2023-07-27 | 0.6793 |  |  | 1957-12-31 | 4.99
2023-07-28 | 0.6669 |  |  | 1958-03-31 | 5.03
2023-07-31 | 0.6682 |  |  | 1958-06-30 | 5.03
2023-08-01 | 0.6673 |  |  | 1958-09-30 | 5.03
2023-08-02 | 0.6581 |  |  | 1958-12-31 | 5.06
2023-08-03 | 0.6538 |  |  | 1959-03-31 | 5.1
2023-08-04 | 0.6573 |  |  | 1959-06-30 | 5.1
2023-08-08 | 0.6531 |  |  | 1959-09-30 | 5.14
2023-08-09 | 0.6556 |  |  | 1959-12-31 | 5.18
2023-08-10 | 0.6545 |  |  | 1960-03-31 | 5.22
2023-08-11 | 0.6522 |  |  | 1960-06-30 | 5.3
2023-08-14 | 0.6475 |  |  | 1960-09-30 | 5.37
2023-08-15 | 0.6512 |  |  | 1960-12-31 | 5.41
2023-08-16 | 0.6451 |  |  | 1961-03-31 | 5.45
2023-08-17 | 0.6385 |  |  | 1961-06-30 | 5.49
2023-08-18 | 0.6407 |  |  | 1961-09-30 | 5.45
2023-08-21 | 0.64 |  |  | 1961-12-31 | 5.45
2023-08-22 | 0.6417 |  |  | 1962-03-31 | 5.45
2023-08-23 | 0.6441 |  |  | 1962-06-30 | 5.45
2023-08-24 | 0.6479 |  |  | 1962-09-30 | 5.45
2023-08-25 | 0.6417 |  |  | 1962-12-31 | 5.45
2023-08-28 | 0.6431 |  |  | 1963-03-31 | 5.45
2023-08-29 | 0.6446 |  |  | 1963-06-30 | 5.45
2023-08-30 | 0.6475 |  |  | 1963-09-30 | 5.49
2023-08-31 | 0.6485 |  |  | 1963-12-31 | 5.49
2023-09-01 | 0.6471 |  |  | 1964-03-31 | 5.53
2023-09-04 | 0.6474 |  |  | 1964-06-30 | 5.57
2023-09-05 | 0.6401 |  |  | 1964-09-30 | 5.64
2023-09-06 | 0.6403 |  |  | 1964-12-31 | 5.68
2023-09-07 | 0.638 |  |  | 1965-03-31 | 5.72
2023-09-08 | 0.6407 |  |  | 1965-06-30 | 5.8
2023-09-11 | 0.6437 |  |  | 1965-09-30 | 5.84
2023-09-12 | 0.6425 |  |  | 1965-12-31 | 5.91
2023-09-13 | 0.6409 |  |  | 1966-03-31 | 5.95
2023-09-14 | 0.6441 |  |  | 1966-06-30 | 5.99
2023-09-15 | 0.6467 |  |  | 1966-09-30 | 5.99
2023-09-18 | 0.6445 |  |  | 1966-12-31 | 6.07
2023-09-19 | 0.6431 |  |  | 1967-03-31 | 6.11
2023-09-20 | 0.6452 |  |  | 1967-06-30 | 6.15
2023-09-21 | 0.6403 |  |  | 1967-09-30 | 6.26
2023-09-22 | 0.6425 |  |  | 1967-12-31 | 6.26
2023-09-25 | 0.6418 |  |  | 1968-03-31 | 6.3
2023-09-26 | 0.6414 |  |  | 1968-06-30 | 6.34
2023-09-27 | 0.6379 |  |  | 1968-09-30 | 6.38
2023-09-28 | 0.6377 |  |  | 1968-12-31 | 6.42
2023-09-29 | 0.6458 |  |  | 1969-03-31 | 6.49
2023-10-03 | 0.6316 |  |  | 1969-06-30 | 6.53
2023-10-04 | 0.6321 |  |  | 1969-09-30 | 6.57
2023-10-05 | 0.6372 |  |  | 1969-12-31 | 6.61
2023-10-06 | 0.6368 |  |  | 1970-03-31 | 6.69
2023-10-09 | 0.635 |  |  | 1970-06-30 | 6.77
2023-10-10 | 0.6411 |  |  | 1970-09-30 | 6.8
2023-10-11 | 0.6421 |  |  | 1970-12-31 | 6.92
2023-10-12 | 0.6423 |  |  | 1971-03-31 | 7
2023-10-13 | 0.6317 |  |  | 1971-06-30 | 7.11
2023-10-16 | 0.6323 |  |  | 1971-09-30 | 7.27
2023-10-17 | 0.6355 |  |  | 1971-12-31 | 7.42
2023-10-18 | 0.6379 |  |  | 1972-03-31 | 7.5
2023-10-19 | 0.6303 |  |  | 1972-06-30 | 7.58
2023-10-20 | 0.6316 |  |  | 1972-09-30 | 7.69
2023-10-23 | 0.6311 |  |  | 1972-12-31 | 7.77
2023-10-24 | 0.6359 |  |  | 1973-03-31 | 7.93
2023-10-25 | 0.6386 |  |  | 1973-06-30 | 8.2
2023-10-26 | 0.6278 |  |  | 1973-09-30 | 8.47
2023-10-27 | 0.6345 |  |  | 1973-12-31 | 8.78
2023-10-30 | 0.6353 |  |  | 1974-03-31 | 9.01
2023-10-31 | 0.6346 |  |  | 1974-06-30 | 9.39
2023-11-01 | 0.6332 |  |  | 1974-09-30 | 9.86
2023-11-02 | 0.6424 |  |  | 1974-12-31 | 10.21
2023-11-03 | 0.6433 |  |  | 1975-03-31 | 10.59
2023-11-06 | 0.651 |  |  | 1975-06-30 | 10.98
2023-11-07 | 0.6439 |  |  | 1975-09-30 | 11.06
2023-11-08 | 0.644 |  |  | 1975-12-31 | 11.68
2023-11-09 | 0.6416 |  |  | 1976-03-31 | 11.98
2023-11-10 | 0.6361 |  |  | 1976-06-30 | 12.29
2023-11-13 | 0.636 |  |  | 1976-09-30 | 12.6
2023-11-14 | 0.6372 |  |  | 1976-12-31 | 13.34
2023-11-15 | 0.65 |  |  | 1977-03-31 | 13.65
2023-11-16 | 0.6471 |  |  | 1977-06-30 | 13.96
2023-11-17 | 0.6468 |  |  | 1977-09-30 | 14.23
2023-11-20 | 0.655 |  |  | 1977-12-31 | 14.57
2023-11-21 | 0.6577 |  |  | 1978-03-31 | 14.77
2023-11-22 | 0.6555 |  |  | 1978-06-30 | 15.08
2023-11-23 | 0.6554 |  |  | 1978-09-30 | 15.35
2023-11-24 | 0.6563 |  |  | 1978-12-31 | 15.7
2023-11-27 | 0.6575 |  |  | 1979-03-31 | 15.97
2023-11-28 | 0.6623 |  |  | 1979-06-30 | 16.39
2023-11-29 | 0.665 |  |  | 1979-09-30 | 16.78
2023-11-30 | 0.6648 |  |  | 1979-12-31 | 17.28
2023-12-01 | 0.6611 |  |  | 1980-03-31 | 17.67
2023-12-04 | 0.6656 |  |  | 1980-06-30 | 18.17
2023-12-05 | 0.6584 |  |  | 1980-09-30 | 18.48
2023-12-06 | 0.6581 |  |  | 1980-12-31 | 18.87
2023-12-07 | 0.6529 |  |  | 1981-03-31 | 19.33
2023-12-08 | 0.6618 |  |  | 1981-06-30 | 19.76
2023-12-11 | 0.6555 |  |  | 1981-09-30 | 20.14
2023-12-12 | 0.6591 |  |  | 1981-12-31 | 20.99
2023-12-13 | 0.6555 |  |  | 1982-03-31 | 21.38
2023-12-14 | 0.6712 |  |  | 1982-06-30 | 21.88
2023-12-15 | 0.6717 |  |  | 1982-09-30 | 22.65
2023-12-18 | 0.6714 |  |  | 1982-12-31 | 23.31
2023-12-19 | 0.6724 |  |  | 1983-03-31 | 23.81
2023-12-20 | 0.6775 |  |  | 1983-06-30 | 24.32
2023-12-21 | 0.6748 |  |  | 1983-09-30 | 24.74
2023-12-22 | 0.6782 |  |  | 1983-12-31 | 25.32
2023-12-27 | 0.6837 |  |  | 1984-03-31 | 25.21
2023-12-28 | 0.6842 |  |  | 1984-06-30 | 25.28
2023-12-29 | 0.684 |  |  | 1984-09-30 | 25.59
2024-01-02 | 0.682 |  |  | 1984-12-31 | 25.98
2024-01-03 | 0.6763 |  |  | 1985-03-31 | 26.33
2024-01-04 | 0.6738 |  |  | 1985-06-30 | 26.95
2024-01-05 | 0.6698 |  |  | 1985-09-30 | 27.56
2024-01-08 | 0.6699 |  |  | 1985-12-31 | 28.11
2024-01-09 | 0.6719 |  |  | 1986-03-31 | 28.76
2024-01-10 | 0.6703 |  |  | 1986-06-30 | 29.23
2024-01-11 | 0.672 |  |  | 1986-09-30 | 30
2024-01-12 | 0.6704 |  |  | 1986-12-31 | 30.85
2024-01-15 | 0.6693 |  |  | 1987-03-31 | 31.47
2024-01-16 | 0.6615 |  |  | 1987-06-30 | 31.93
2024-01-17 | 0.6571 |  |  | 1987-09-30 | 32.47
2024-01-18 | 0.6558 |  |  | 1987-12-31 | 33.05
2024-01-19 | 0.6579 |  |  | 1988-03-31 | 33.63
2024-01-22 | 0.6594 |  |  | 1988-06-30 | 34.21
2024-01-23 | 0.6602 |  |  | 1988-09-30 | 34.87
2024-01-24 | 0.6575 |  |  | 1988-12-31 | 35.57
2024-01-25 | 0.6575 |  |  | 1989-03-31 | 35.91
2024-01-29 | 0.659 |  |  | 1989-06-30 | 36.8
2024-01-30 | 0.6609 |  |  | 1989-09-30 | 37.65
2024-01-31 | 0.6574 |  |  | 1989-12-31 | 38.35
2024-02-01 | 0.6553 |  |  | 1990-03-31 | 39.01
2024-02-02 | 0.6597 |  |  | 1990-06-30 | 39.63
2024-02-05 | 0.6508 |  |  | 1990-09-30 | 39.94
2024-02-06 | 0.6515 |  |  | 1990-12-31 | 40.98
2024-02-07 | 0.6529 |  |  | 1991-03-31 | 40.9
2024-02-08 | 0.6523 |  |  | 1991-06-30 | 40.98
2024-02-09 | 0.6492 |  |  | 1991-09-30 | 41.21
2024-02-12 | 0.6518 |  |  | 1991-12-31 | 41.6
2024-02-13 | 0.6516 |  |  | 1992-03-31 | 41.6
2024-02-14 | 0.6464 |  |  | 1992-06-30 | 41.48
2024-02-15 | 0.6485 |  |  | 1992-09-30 | 41.52
2024-02-16 | 0.6518 |  |  | 1992-12-31 | 41.71
2024-02-19 | 0.6544 |  |  | 1993-03-31 | 42.1
2024-02-20 | 0.6531 |  |  | 1993-06-30 | 42.25
2024-02-21 | 0.6568 |  |  | 1993-09-30 | 42.45
2024-02-22 | 0.6559 |  |  | 1993-12-31 | 42.53
2024-02-23 | 0.6572 |  |  | 1994-03-31 | 42.68
2024-02-26 | 0.6557 |  |  | 1994-06-30 | 42.99
2024-02-27 | 0.6544 |  |  | 1994-09-30 | 43.26
2024-02-28 | 0.6519 |  |  | 1994-12-31 | 43.61
2024-02-29 | 0.6519 |  |  | 1995-03-31 | 44.34
2024-03-01 | 0.651 |  |  | 1995-06-30 | 44.92
2024-03-04 | 0.652 |  |  | 1995-09-30 | 45.46
2024-03-05 | 0.6502 |  |  | 1995-12-31 | 45.81
2024-03-06 | 0.6514 |  |  | 1996-03-31 | 46
2024-03-07 | 0.6586 |  |  | 1996-06-30 | 46.31
2024-03-08 | 0.6626 |  |  | 1996-09-30 | 46.43
2024-03-11 | 0.6611 |  |  | 1996-12-31 | 46.51
2024-03-12 | 0.6615 |  |  | 1997-03-31 | 46.58
2024-03-13 | 0.6614 |  |  | 1997-06-30 | 46.47
2024-03-14 | 0.6616 |  |  | 1997-09-30 | 46.28
2024-03-15 | 0.6567 |  |  | 1997-12-31 | 46.39
2024-03-18 | 0.6566 |  |  | 1998-03-31 | 46.51
2024-03-19 | 0.6529 |  |  | 1998-06-30 | 46.78
2024-03-20 | 0.6526 |  |  | 1998-09-30 | 46.91
2024-03-21 | 0.6624 |  |  | 1998-12-31 | 47.11
2024-03-22 | 0.6525 |  |  | 1999-03-31 | 47.08
2024-03-25 | 0.6528 |  |  | 1999-06-30 | 47.29
2024-03-26 | 0.6539 |  |  | 1999-09-30 | 47.72
2024-03-27 | 0.6529 |  |  | 1999-12-31 | 47.97
2024-03-28 | 0.6532 |  |  | 2000-03-31 | 48.4
2024-04-02 | 0.649 |  |  | 2000-06-30 | 48.77
2024-04-03 | 0.6519 |  |  | 2000-09-30 | 50.59
2024-04-04 | 0.6587 |  |  | 2000-12-31 | 50.76
2024-04-05 | 0.6572 |  |  | 2001-03-31 | 51.3
2024-04-08 | 0.6579 |  |  | 2001-06-30 | 51.73
2024-04-09 | 0.6608 |  |  | 2001-09-30 | 51.87
2024-04-10 | 0.6621 |  |  | 2001-12-31 | 52.35
2024-04-11 | 0.6523 |  |  | 2002-03-31 | 52.82
2024-04-12 | 0.6526 |  |  | 2002-06-30 | 53.2
2024-04-15 | 0.6488 |  |  | 2002-09-30 | 53.56
2024-04-16 | 0.6426 |  |  | 2002-12-31 | 53.92
2024-04-17 | 0.6408 |  |  | 2003-03-31 | 54.62
2024-04-18 | 0.6448 |  |  | 2003-06-30 | 54.62
2024-04-19 | 0.6397 |  |  | 2003-09-30 | 54.93
2024-04-22 | 0.6434 |  |  | 2003-12-31 | 55.22
2024-04-23 | 0.6455 |  |  | 2004-03-31 | 55.71
2024-04-24 | 0.6519 |  |  | 2004-06-30 | 55.97
2024-04-26 | 0.6539 |  |  | 2004-09-30 | 56.2
2024-04-29 | 0.6569 |  |  | 2004-12-31 | 56.63
2024-04-30 | 0.6525 |  |  | 2005-03-31 | 57.01
2024-05-01 | 0.6475 |  |  | 2005-06-30 | 57.35
2024-05-02 | 0.6541 |  |  | 2005-09-30 | 57.92
2024-05-03 | 0.6579 |  |  | 2005-12-31 | 58.22
2024-05-06 | 0.6613 |  |  | 2006-03-31 | 58.72
2024-05-07 | 0.66 |  |  | 2006-06-30 | 59.65
2024-05-08 | 0.6579 |  |  | 2006-09-30 | 60.18
2024-05-09 | 0.6577 |  |  | 2006-12-31 | 60.11
2024-05-10 | 0.661 |  |  | 2007-03-31 | 60.16
2024-05-13 | 0.6596 |  |  | 2007-06-30 | 60.9
2024-05-14 | 0.66 |  |  | 2007-09-30 | 61.32
2024-05-15 | 0.6648 |  |  | 2007-12-31 | 61.89
2024-05-16 | 0.6679 |  |  | 2008-03-31 | 62.72
2024-05-17 | 0.6673 |  |  | 2008-06-30 | 63.63
2024-05-20 | 0.6704 |  |  | 2008-09-30 | 64.37
2024-05-21 | 0.6658 |  |  | 2008-12-31 | 64.16
2024-05-22 | 0.6674 |  |  | 2009-03-31 | 64.23
2024-05-23 | 0.6621 |  |  | 2009-06-30 | 64.55
2024-05-24 | 0.66 |  |  | 2009-09-30 | 65.16
2024-05-27 | 0.6634 |  |  | 2009-12-31 | 65.51
2024-05-28 | 0.6667 |  |  | 2010-03-31 | 66.12
2024-05-29 | 0.6647 |  |  | 2010-06-30 | 66.52
2024-05-30 | 0.6597 |  |  | 2010-09-30 | 67
2024-05-31 | 0.6637 |  |  | 2010-12-31 | 67.26
2024-06-03 | 0.6646 |  |  | 2011-03-31 | 68.3
2024-06-04 | 0.6668 |  |  | 2011-06-30 | 68.93
2024-06-05 | 0.6658 |  |  | 2011-09-30 | 69.34
2024-06-06 | 0.666 |  |  | 2011-12-31 | 69.34
2024-06-07 | 0.6672 |  |  | 2012-03-31 | 69.38
2024-06-11 | 0.6602 |  |  | 2012-06-30 | 69.74
2024-06-12 | 0.6621 |  |  | 2012-09-30 | 70.69
2024-06-13 | 0.6642 |  |  | 2012-12-31 | 70.87
2024-06-14 | 0.6626 |  |  | 2013-03-31 | 71.11
2024-06-17 | 0.6601 |  |  | 2013-06-30 | 71.38
2024-06-18 | 0.6626 |  |  | 2013-09-30 | 72.25
2024-06-19 | 0.667 |  |  | 2013-12-31 | 72.77
2024-06-20 | 0.6669 |  |  | 2014-03-31 | 73.2
2024-06-21 | 0.6665 |  |  | 2014-06-30 | 73.57
2024-06-24 | 0.6641 |  |  | 2014-09-30 | 73.88
2024-06-25 | 0.6664 |  |  | 2014-12-31 | 74.02
2024-06-26 | 0.6686 |  |  | 2015-03-31 | 74.16
2024-06-27 | 0.6666 |  |  | 2015-06-30 | 74.69
2024-06-28 | 0.6624 |  |  | 2015-09-30 | 74.98
2024-07-01 | 0.6668 |  |  | 2015-12-31 | 75.27
2024-07-02 | 0.6646 |  |  | 2016-03-31 | 75.12
2024-07-03 | 0.6673 |  |  | 2016-06-30 | 75.45
2024-07-04 | 0.6717 |  |  | 2016-09-30 | 75.98
2024-07-05 | 0.6734 |  |  | 2016-12-31 | 76.38
2024-07-08 | 0.6744 |  |  | 2017-03-31 | 76.73
2024-07-09 | 0.6744 |  |  | 2017-06-30 | 76.88
2024-07-10 | 0.6744 |  |  | 2017-09-30 | 77.35
2024-07-11 | 0.6761 |  |  | 2017-12-31 | 77.87
2024-07-12 | 0.6772 |  |  | 2018-03-31 | 78.21
2024-07-15 | 0.6775 |  |  | 2018-06-30 | 78.49
2024-07-16 | 0.6738 |  |  | 2018-09-30 | 78.83
2024-07-17 | 0.6736 |  |  | 2018-12-31 | 79.24
2024-07-18 | 0.6739 |  |  | 2019-03-31 | 79.23
2024-07-19 | 0.6701 |  |  | 2019-06-30 | 79.7
2024-07-22 | 0.6663 |  |  | 2019-09-30 | 80.15
2024-07-23 | 0.6633 |  |  | 2019-12-31 | 80.7
2024-07-24 | 0.6595 |  |  | 2020-03-31 | 81
2024-07-25 | 0.6546 |  |  | 2020-06-30 | 79.44
2024-07-26 | 0.6555 |  |  | 2020-09-30 | 80.67
2024-07-29 | 0.6552 |  |  | 2020-12-31 | 81.4
2024-07-30 | 0.6556 |  |  | 2021-03-31 | 81.87
2024-07-31 | 0.6491 |  |  | 2021-06-30 | 82.47
2024-08-01 | 0.6534 |  |  | 2021-09-30 | 83.17
2024-08-02 | 0.6515 |  |  | 2021-12-31 | 84.23
2024-08-06 | 0.6511 |  |  | 2022-03-31 | 86.05
2024-08-07 | 0.6551 |  |  | 2022-06-30 | 87.59
2024-08-08 | 0.6552 |  |  | 2022-09-30 | 89.2
2024-08-09 | 0.6592 |  |  | 2022-12-31 | 90.85
2024-08-12 | 0.6582 |  |  | 2023-03-31 | 92.08
2024-08-13 | 0.6594 |  |  | 2023-06-30 | 92.87
2024-08-14 | 0.6634 |  |  | 2023-09-30 | 93.94
2024-08-15 | 0.662 |  |  | 2023-12-31 | 94.53
2024-08-16 | 0.663 |  |  | 2024-03-31 | 95.41
2024-08-19 | 0.6684 |  |  | 2024-06-30 | 96.41
2024-08-20 | 0.6719 |  |  | 2024-09-30 | 96.62
2024-08-21 | 0.6742 |  |  | 2024-12-31 | 96.81
2024-08-22 | 0.674 |  |  | 2025-03-31 | 97.7
2024-08-23 | 0.672 |  |  | 2025-06-30 | 98.43
2024-08-26 | 0.6776 |  |  | 2025-09-30 | 99.73
2024-08-27 | 0.6787 |  |  | 2025-12-31 | 100.32
2024-08-28 | 0.6789 |  |  | 2026-03-31 | 101.7
2024-08-29 | 0.6807
2024-08-30 | 0.6806
2024-09-02 | 0.6766
2024-09-03 | 0.6741
2024-09-04 | 0.6704
2024-09-05 | 0.6723
2024-09-06 | 0.6724
2024-09-09 | 0.6668
2024-09-10 | 0.6668
2024-09-11 | 0.6659
2024-09-12 | 0.6693
2024-09-13 | 0.6722
2024-09-16 | 0.6727
2024-09-17 | 0.6748
2024-09-18 | 0.6761
2024-09-19 | 0.6801
2024-09-20 | 0.6818
2024-09-23 | 0.6828
2024-09-24 | 0.6839
2024-09-25 | 0.688
2024-09-26 | 0.6863
2024-09-27 | 0.6878
2024-09-30 | 0.6932
2024-10-01 | 0.6928
2024-10-02 | 0.688
2024-10-03 | 0.6865
2024-10-04 | 0.6848
2024-10-08 | 0.6739
2024-10-09 | 0.6746
2024-10-10 | 0.6739
2024-10-11 | 0.6744
2024-10-14 | 0.6738
2024-10-15 | 0.6711
2024-10-16 | 0.6691
2024-10-17 | 0.6691
2024-10-18 | 0.6702
2024-10-21 | 0.6705
2024-10-22 | 0.6687
2024-10-23 | 0.6677
2024-10-24 | 0.6648
2024-10-25 | 0.6621
2024-10-28 | 0.6591
2024-10-29 | 0.6565
2024-10-30 | 0.6543
2024-10-31 | 0.6569
2024-11-01 | 0.6576
2024-11-04 | 0.6609
2024-11-05 | 0.6594
2024-11-06 | 0.6543
2024-11-07 | 0.6622
2024-11-08 | 0.6654
2024-11-11 | 0.6594
2024-11-12 | 0.6555
2024-11-13 | 0.6537
2024-11-14 | 0.6471
2024-11-15 | 0.6466
2024-11-18 | 0.6472
2024-11-19 | 0.6508
2024-11-20 | 0.6528
2024-11-21 | 0.6517
2024-11-22 | 0.6504
2024-11-25 | 0.6525
2024-11-26 | 0.6493
2024-11-27 | 0.6476
2024-11-28 | 0.6492
2024-11-29 | 0.6517
2024-12-02 | 0.6496
2024-12-03 | 0.6469
2024-12-04 | 0.6438
2024-12-05 | 0.6433
2024-12-06 | 0.643
2024-12-09 | 0.6382
2024-12-10 | 0.6385
2024-12-11 | 0.6374
2024-12-12 | 0.6417
2024-12-13 | 0.6367
2024-12-16 | 0.6377
2024-12-17 | 0.6356
2024-12-18 | 0.6313
2024-12-19 | 0.6226
2024-12-20 | 0.6226
2024-12-23 | 0.6259
2024-12-24 | 0.624
2024-12-27 | 0.6211
2024-12-30 | 0.6241
2024-12-31 | 0.6217
2025-01-02 | 0.6217
2025-01-03 | 0.6216
2025-01-06 | 0.6223
2025-01-07 | 0.6259
2025-01-08 | 0.623
2025-01-09 | 0.6199
2025-01-10 | 0.6194
2025-01-13 | 0.6133
2025-01-14 | 0.6189
2025-01-15 | 0.6195
2025-01-16 | 0.6206
2025-01-17 | 0.62
2025-01-20 | 0.6214
2025-01-21 | 0.6249
2025-01-22 | 0.6265
2025-01-23 | 0.6275
2025-01-24 | 0.6316
2025-01-28 | 0.6253
2025-01-29 | 0.6237
2025-01-30 | 0.6225
2025-01-31 | 0.6225
2025-02-03 | 0.6116
2025-02-04 | 0.619
2025-02-05 | 0.6249
2025-02-06 | 0.6263
2025-02-07 | 0.6284
2025-02-10 | 0.6272
2025-02-11 | 0.6275
2025-02-12 | 0.629
2025-02-13 | 0.6296
2025-02-14 | 0.6321
2025-02-17 | 0.6369
2025-02-18 | 0.6353
2025-02-19 | 0.6364
2025-02-20 | 0.6363
2025-02-21 | 0.6397
2025-02-24 | 0.6381
2025-02-25 | 0.6351
2025-02-26 | 0.6328
2025-02-27 | 0.6288
2025-02-28 | 0.6214
2025-03-03 | 0.622
2025-03-04 | 0.6191
2025-03-05 | 0.625
2025-03-06 | 0.6347
2025-03-07 | 0.6306
2025-03-10 | 0.6307
2025-03-11 | 0.6277
2025-03-12 | 0.6289
2025-03-13 | 0.631
2025-03-14 | 0.6294
2025-03-17 | 0.6326
2025-03-18 | 0.6375
2025-03-19 | 0.6357
2025-03-20 | 0.6344
2025-03-21 | 0.6289
2025-03-24 | 0.6278
2025-03-25 | 0.6287
2025-03-26 | 0.6311
2025-03-27 | 0.6313
2025-03-28 | 0.6284
2025-03-31 | 0.628
2025-04-01 | 0.6269
2025-04-02 | 0.6299
2025-04-03 | 0.6266
2025-04-04 | 0.6234
2025-04-07 | 0.6017
2025-04-08 | 0.6069
2025-04-09 | 0.5975
2025-04-10 | 0.6199
2025-04-11 | 0.6197
2025-04-14 | 0.6303
2025-04-15 | 0.6352
2025-04-16 | 0.6353
2025-04-17 | 0.6341
2025-04-22 | 0.6437
2025-04-23 | 0.6398
2025-04-24 | 0.6347
2025-04-28 | 0.6404
2025-04-29 | 0.6413
2025-04-30 | 0.6416
2025-05-01 | 0.6394
2025-05-02 | 0.6411
2025-05-05 | 0.6479
2025-05-06 | 0.6453
2025-05-07 | 0.6484
2025-05-08 | 0.6445
2025-05-09 | 0.6407
2025-05-12 | 0.6439
2025-05-13 | 0.6409
2025-05-14 | 0.6472
2025-05-15 | 0.6426
2025-05-16 | 0.6436
2025-05-19 | 0.6402
2025-05-20 | 0.6416
2025-05-21 | 0.6452
2025-05-22 | 0.6448
2025-05-23 | 0.6437
2025-05-26 | 0.6527
2025-05-27 | 0.6481
2025-05-28 | 0.6436
2025-05-29 | 0.6421
2025-05-30 | 0.6436
2025-06-02 | 0.6458
2025-06-03 | 0.6464
2025-06-04 | 0.6458
2025-06-05 | 0.649
2025-06-06 | 0.6501
2025-06-10 | 0.6505
2025-06-11 | 0.6518
2025-06-12 | 0.6504
2025-06-13 | 0.6475
2025-06-16 | 0.6499
2025-06-17 | 0.6531
2025-06-18 | 0.6504
2025-06-19 | 0.6466
2025-06-20 | 0.6492
2025-06-23 | 0.6412
2025-06-24 | 0.6498
2025-06-25 | 0.65
2025-06-26 | 0.6528
2025-06-27 | 0.6543
2025-06-30 | 0.655
2025-07-01 | 0.6579
2025-07-02 | 0.6577
2025-07-03 | 0.6572
2025-07-04 | 0.6571
2025-07-07 | 0.651
2025-07-08 | 0.6539
2025-07-09 | 0.6534
2025-07-10 | 0.6549
2025-07-11 | 0.658
2025-07-14 | 0.6561
2025-07-15 | 0.6555
2025-07-16 | 0.6528
2025-07-17 | 0.6488
2025-07-18 | 0.6502
2025-07-21 | 0.6514
2025-07-22 | 0.6513
2025-07-23 | 0.6568
2025-07-24 | 0.6621
2025-07-25 | 0.6581
2025-07-28 | 0.6564
2025-07-29 | 0.6525
2025-07-30 | 0.6511
2025-07-31 | 0.6469
2025-08-01 | 0.6435
2025-08-05 | 0.6459
2025-08-06 | 0.6487
2025-08-07 | 0.6517
2025-08-08 | 0.6519
2025-08-11 | 0.6526
2025-08-12 | 0.6498
2025-08-13 | 0.6532
2025-08-14 | 0.6549
2025-08-15 | 0.6505
2025-08-18 | 0.652
2025-08-19 | 0.6479
2025-08-20 | 0.645
2025-08-21 | 0.6426
2025-08-22 | 0.6417
2025-08-25 | 0.6494
2025-08-26 | 0.6482
2025-08-27 | 0.6487
2025-08-28 | 0.651
2025-08-29 | 0.6538
2025-09-01 | 0.6544
2025-09-02 | 0.6538
2025-09-03 | 0.6514
2025-09-04 | 0.6525
2025-09-05 | 0.6537
2025-09-08 | 0.6566
2025-09-09 | 0.6614
2025-09-10 | 0.661
2025-09-11 | 0.6604
2025-09-12 | 0.6658
2025-09-15 | 0.6661
2025-09-16 | 0.6667
2025-09-17 | 0.6678
2025-09-18 | 0.6624
2025-09-19 | 0.6596
2025-09-22 | 0.6593
2025-09-23 | 0.6589
2025-09-24 | 0.6625
2025-09-25 | 0.6595
2025-09-26 | 0.654
2025-09-29 | 0.6571
2025-09-30 | 0.6602
2025-10-01 | 0.6601
2025-10-02 | 0.6619
2025-10-03 | 0.6591
2025-10-07 | 0.6612
2025-10-08 | 0.6564
2025-10-09 | 0.6608
2025-10-10 | 0.6568
2025-10-13 | 0.6524
2025-10-14 | 0.648
2025-10-15 | 0.6516
2025-10-16 | 0.6492
2025-10-17 | 0.6475
2025-10-20 | 0.6503
2025-10-21 | 0.6504
2025-10-22 | 0.6501
2025-10-23 | 0.6486
2025-10-24 | 0.6502
2025-10-27 | 0.6533
2025-10-28 | 0.6564
2025-10-29 | 0.6596
2025-10-30 | 0.6595
2025-10-31 | 0.6551
2025-11-03 | 0.6554
2025-11-04 | 0.6532
2025-11-05 | 0.6492
2025-11-06 | 0.6514
2025-11-07 | 0.6476
2025-11-10 | 0.6525
2025-11-11 | 0.6524
2025-11-12 | 0.6521
2025-11-13 | 0.6557
2025-11-14 | 0.6533
2025-11-17 | 0.6523
2025-11-18 | 0.6481
2025-11-19 | 0.6484
2025-11-20 | 0.6487
2025-11-21 | 0.6446
2025-11-24 | 0.6461
2025-11-25 | 0.6454
2025-11-26 | 0.6503
2025-11-27 | 0.6536
2025-11-28 | 0.6533
2025-12-01 | 0.6545
2025-12-02 | 0.655
2025-12-03 | 0.658
2025-12-04 | 0.6614
2025-12-05 | 0.662
2025-12-08 | 0.6645
2025-12-09 | 0.6647
2025-12-10 | 0.6641
2025-12-11 | 0.6639
2025-12-12 | 0.6661
2025-12-15 | 0.6646
2025-12-16 | 0.6637
2025-12-17 | 0.6616
2025-12-18 | 0.6602
2025-12-19 | 0.6609
2025-12-22 | 0.6628
2025-12-23 | 0.6669
2025-12-24 | 0.6709
2025-12-29 | 0.6722
2025-12-30 | 0.6711
2025-12-31 | 0.6693
2026-01-02 | 0.6699
2026-01-05 | 0.6673
2026-01-06 | 0.6726
2026-01-07 | 0.6761
2026-01-08 | 0.6707
2026-01-09 | 0.6698
2026-01-12 | 0.6696
2026-01-13 | 0.6711
2026-01-14 | 0.6697
2026-01-15 | 0.6675
2026-01-16 | 0.6707
2026-01-19 | 0.6692
2026-01-20 | 0.6738
2026-01-21 | 0.6733
2026-01-22 | 0.6805
2026-01-23 | 0.685
2026-01-27 | 0.6912
2026-01-28 | 0.6993
2026-01-29 | 0.7091
2026-01-30 | 0.7004
2026-02-02 | 0.6942
2026-02-03 | 0.701
2026-02-04 | 0.7024
2026-02-05 | 0.6972
2026-02-06 | 0.6944
2026-02-09 | 0.7025
2026-02-10 | 0.7075
2026-02-11 | 0.7112
2026-02-12 | 0.7116
2026-02-13 | 0.7086
2026-02-16 | 0.7087
2026-02-17 | 0.7069
2026-02-18 | 0.707
2026-02-19 | 0.7051
2026-02-20 | 0.7033
2026-02-23 | 0.7071
2026-02-24 | 0.706
2026-02-25 | 0.7107
2026-02-26 | 0.7127
2026-02-27 | 0.7126
2026-03-02 | 0.7094
2026-03-03 | 0.7104
2026-03-04 | 0.6996
2026-03-05 | 0.7053
2026-03-06 | 0.7029
2026-03-09 | 0.6993
2026-03-10 | 0.7063
2026-03-11 | 0.7183
2026-03-12 | 0.7125
2026-03-13 | 0.7063
2026-03-16 | 0.7007
2026-03-17 | 0.7074
2026-03-18 | 0.7115
2026-03-19 | 0.7038
2026-03-20 | 0.7088
2026-03-23 | 0.698
2026-03-24 | 0.6966
2026-03-25 | 0.6974
2026-03-26 | 0.6955
2026-03-27 | 0.6911
2026-03-30 | 0.6869
2026-03-31 | 0.6845
2026-04-01 | 0.6904
2026-04-02 | 0.6879
2026-04-07 | 0.6916
2026-04-08 | 0.7072
2026-04-09 | 0.7036
2026-04-10 | 0.7071
2026-04-13 | 0.704
2026-04-14 | 0.7083
2026-04-15 | 0.7138
2026-04-16 | 0.7189
2026-04-17 | 0.717
2026-04-20 | 0.7149
2026-04-21 | 0.7166
2026-04-22 | 0.717
2026-04-23 | 0.7155
2026-04-24 | 0.7128
2026-04-28 | 0.7172
2026-04-29 | 0.7162
2026-04-30 | 0.7113
2026-05-01 | 0.7191
2026-05-04 | 0.7208
2026-05-05 | 0.7141
2026-05-06 | 0.7248
2026-05-07 | 0.7247
2026-05-08 | 0.7225
2026-05-11 | 0.7231
2026-05-12 | 0.7231
2026-05-13 | 0.724
2026-05-14 | 0.7258
2026-05-15 | 0.716
2026-05-18 | 0.7132
2026-05-19 | 0.7132
2026-05-20 | 0.7103
2026-05-21 | 0.7125
2026-05-22 | 0.7139
2026-05-25 | 0.7166
2026-05-26 | 0.716
2026-05-27 | 0.7156
2026-05-28 | 0.7117
2026-05-29 | 0.7164
2026-06-01 | 0.7188
2026-06-02 | 0.7163
2026-06-03 | 0.7164
2026-06-04 | 0.7131
2026-06-05 | 0.7121
2026-06-09 | 0.7058
2026-06-10 | 0.702
2026-06-11 | 0.7008
2026-06-12 | 0.7029
2026-06-15 | 0.7081
2026-06-16 | 0.7048
2026-06-17 | 0.7059
2026-06-18 | 0.7031
2026-06-19 | 0.7005
2026-06-22 | 0.7004
2026-06-23 | 0.6964
2026-06-24 | 0.6913
2026-06-25 | 0.6892
2026-06-26 | 0.6894
2026-06-29 | 0.6896
2026-06-30 | 0.6869
2026-07-01 | 0.6895
2026-07-02 | 0.6894
2026-07-03 | 0.6941
2026-07-06 | 0.6931
2026-07-07 | 0.6942
2026-07-08 | 0.6943
2026-07-09 | 0.6941
2026-07-10 | 0.6949
2026-07-13 | 0.693
2026-07-14 | 0.6935
2026-07-15 | 0.6988
2026-07-16 | 0.6997
2026-07-17 | 0.698
2026-07-20 | 0.6991
2026-07-21 | 0.7009

## IASR
2026 ISP Inputs and Assumptions Workbook
2026-06-25
https://www.aemo.com.au/-/media/files/major-publications/isp/2026/supporting-materials/2026-isp-inputs-and-assumptions-workbook.xlsm?rev=de6f5853cd5e4d5cbb06bc90bdf0e378&sc_lang=en
Filtered to only include relevant technologies, and for 'Step change'
Capital cost projections ($/kW, real 2025 dollars)
Cost to construct new generation, excluding connection costs where these are provided in the Connection cost tab.
These capital cost trajectories are developed by CSIRO's GALLM (see GenCost 2025-26 Consultation draft for more details) based on the technology specific capital cost estimates provided by GHD (2025 Energy Technology Cost and Technical Parameter Review).
To calculate the capital costs of these technologies elsewhere in Australia, multiply these capacital cost with the appropriate locational cost factor given in the Locational Cost Factors worksheet.
The build costs do not include costs associated with expanded transmission access or additional costs incurred when development within a REZ exceeds technology limits. Details on these additional costs are found in the Build limits tab.
The financial years in table are mapped to the preceding calendar year in the GenCost 2025-26 Consultation Draft.
Build costs |  |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8
Technology1 | GenCost Scenario | IASR Scenario | Source | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2026-27 cost excluding land and connections | Calculated. Applied since Thermoflow costs do not include these elements and they are applied later
OCGT (small GT) | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 2914 | 2777 | 2645 | 2523 | 2412 | 2309 | 2429.7686
OCGT (large GT) | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 1764 | 1681 | 1602 | 1528 | 1460 | 1398 | 1438.6076
Gas recip | GenCost Global NZE post 2050 |  |  |  | 2022 | 2022 | 2012 | 2012 | 2015 | 2019 | 1809.7497 | Not in IASR. Taken from CSIRO GenCost 2025_26
CCGT | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 2497 | 2433 | 2370 | 2308 | 2250 | 2194 | 2177.6068
Large scale Solar PV | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 1621 | 1381 | 1187 | 1066 | 989 | 930 | 1302.8302
Battery storage (4hrs storage) | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 1540 | 1424 | 1332 | 1264 | 1208 | 1180 | 1381.378
Battery storage (6hrs storage) |  |  |  |  | 2002 | 1852 | 1738 | 1648 | 1576 | 1538 | 1807.1356 | Interpolated
Battery storage (7hrs storage) |  |  |  |  | 2233 | 2066 | 1941 | 1840 | 1760 | 1717 | 2021.8461 | Interpolated
Battery storage (8hrs storage) | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 2464 | 2280 | 2144 | 2032 | 1944 | 1896 | 2237.7778
Wind | GenCost Global NZE post 2050 | Step Change | CSIRO GenCost 2025-26 Consultation Draft | Not Applicable | 3248 | 3112 | 2981 | 2860 | 2745 | 2638 | 3036.0976
1. To reflect short-term cost pressures, BOTN (Cethana) has been adjusted using the same factor applied to Pumped Hydro (24hrs storage) in GenCost 2024-25 Final report.
2. The capital cost for Distributed Resources Solar and Distributed Resources Batteries, as provided in the Aurecon 2024 Energy Technology Cost and Technical Parameter Review, are assumed to have the same trajectory as that of their transmission-connected counterparts.
3. AEMO will add an additonal cost to the overnight capital cost of Alkaline Electrolysers as stated in this table to represent cost associated with pipelines.
4. Distributed Resources Solar and Distributed Resources Batteries are alternate names for mid-scale generation and storage.
Fixed operating and maintenance cost (real 2025 dollars)
Costs that are incurred regardless of energy generated.
New entrant technologies
Technology Type | Base value ($/kW/year))
OCGT (small GT) | 17.6858
OCGT (large GT) | 14.3234
Gas recip | 29.4 | Not in IASR. Taken from CSIRO GenCost 2025_26
CCGT | 15.303
Large scale Solar PV | 12.2196
Battery storage (4hrs storage) | 21.588
Battery storage (6hrs storage) | 29.7853 | Interpolated
Battery storage (7hrs storage) | 33.8839 | Interpolated
Battery storage (8hrs storage) | 37.9826
Wind | 28.5124
Notes:
1. Sourced from Aurecon 2024 Energy Technology Cost and Technical Parameter Review including cost escalation.
2. Wind, Large-Scale Solar PV and Solar Thermal Variable O&M costs are assumed to be included in the Fixed O&M costs as per Aurecon's report.
3. The cost of extended warranties are included in the Fixed O&M costs for Battery storage to cover a 20-year battery life.
Variable operating and maintenance cost (real 2025 dollars)
Costs that can be expressed in terms of energy generated, not including fuel costs.
New entrant technologies
Generator | Base value
OCGT (small GT) | 16.3946
OCGT (large GT) | 8.2482
Gas recip | 20 | Not in IASR. Jacobs
CCGT | 4.175
Large scale Solar PV | 0
Battery storage (4hrs storage) | 0
Battery storage (6hrs storage) | 0 | Interpolated
Battery storage (7hrs storage) | 0 | Interpolated
Battery storage (8hrs storage) | 0
Wind | 0
Notes:
1. Sourced from Aurecon 2024 Energy Technology Cost and Technical Parameter Review, cost adjusted.
2. Wind, Large-scale Solar PV, Solar Thermal, Pumped Hydro and Electrolyser O&M costs are assumed
to be included in the Fixed O&M costs as per Aurecon's report.
Technology cost breakdown ratios
Technology | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs | Topographical cost |  | Instalation costs excl land and connections | Calculated. Applied since Thermoflow costs do not include these elements and they are applied later
OCGT (small GT) | 61.25% | 4.629% | 7.875% | 26.25% | Not Applicable |  | 30%
OCGT (large GT) | 59.91% | 6.717% | 7.702% | 25.67% | Not Applicable |  | 30%
Gas recip | 61.25% | 4.629% | 7.875% | 26.25% | Not Applicable |  | 30% | Not in IASR. Assumed sim to small GT
CCGT | 62.65% | 2.442% | 8.055% | 26.85% | Not Applicable |  | 30%
Large scale Solar PV | 56.6% | 0% | 5.66% | 37.74% | Not Applicable |  | 40%
Battery storage (4hrs storage) | 80.4% | 0% | 2.993% | 16.61% | Not Applicable |  | 17.12%
Battery storage (6hrs storage) | 80.87% | 0% | 2.422% | 16.7% |  |  | 17.12% | Interpolated
Battery storage (7hrs storage) | 81.11% | 0% | 2.137% | 16.75% |  |  | 17.12% | Interpolated
Battery Storage (8hrs storage) | 81.35% | 0% | 1.852% | 16.8% | Not Applicable |  | 17.11%
Wind | 70.38% | 0% | 2.439% | 27.18% | Not Applicable |  | 27.86%
Notes:
1. Calculated from technology component costs provided in Aurecon 2024 Energy Technology Cost and Technical Parameter Review.
Lead time and project life
Development lead time considers the time necessary to undertake feasibility studies, secure necessary development approvals, and to construct the project. For capacity planning therefore, the lead time reflects the shortest time before a technology can commence operation.
Parameters for all technologies are sourced from Aurecon 2024 Energy Technology Cost and Technical Parameter Review.
Technology | Lead time for development (years)1, 2 | Lead time (years)3 | Construction time (years) | Total lead time (years)4,7 | Economic life (years)5 | Technical life (years)6
OCGT (small GT) | 2 | 2 | 1.5 | 6 | 25 | 40
OCGT (large GT) | 2 | 2 | 1.1154 | 5 | 25 | 40
Gas recip | 2 | 1 | 1 | 4 | 25 | 25 | Not in IASR. Jacobs
CCGT | 2.5 | 1.75 | 1.5 | 6 | 25 | 40
Large scale Solar PV | 0 | 1 | 0.5 | 2 | 30 | 30
Battery storage (4hrs storage) | 0 | 1.4 | 1.1538 | 3 | 20 | 20
Battery storage (6hrs storage) | 0 | 1.5 | 1.2308 | 3 | 20 | 20 | Interpolated
Battery storage (7hrs storage) | 0 | 1.55 | 1.2692 | 3 | 20 | 20 | Interpolated
Battery storage (8hrs storage) | 0 | 1.6 | 1.3077 | 3 | 20 | 20
Wind | 0 | 1 | 1.7308 | 3 | 25 | 30
Notes:
1. Aurecon has assumed that lead time for development is the time to undertake feasibility studies, procurement and contract negotiations, obtain permits and approvals, secure land agreements, fuel supply and obtain financing.
2. Given existing development activity in these technologies, AEMO has assumed no lead time for development for onshore wind, batteries, large-scale solar PV, Distributed Resources Solar,and Distributed Resources Batteries.
3. Aurecon has assumed lead time as the time from issue of Notice to Proceed (NTP) to the EPC contractor up to the delivery of all major equipment to site.
4. Aurecon has provided some components of lead time in weeks or fractions of years. AEMO has rounded the total lead time to the nearest whole number of years.
5. Period of time required for the project to pay off its build costs.
6. Period of time the project is operational before life extension refurbishment or retirement may be required.
7. AEMO proposes to apply the total leadtime from the date of the Generation Information that is used in the ISP modelling

## TFlow33
GT PRO Classic 33.0
Program revision date: July 17, 2026
Note: Cost reference date is March 2025 for most configurations in current database
PEACE: |  |  | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | CCGT | CCGT | CCGT | CCGT | RECIP | RECIP | RECIP | RECIP
|  |  | GT13E2 | GT13E2 | SGT5-2000E | SGT5-2000E | 1x9FA | 1x9FA | LM2500 | LM2500 | LM6000 | LM6000 | LMS100 | LMS100 | 9FA | 9FA | GT13E2 | GT13E2 | Jenbacher | Jenbacher | Wartsila | Wartsila
|  |  | DF | GasOnly | DF | GasOnly | DF | GasOnly | GasOnly | DF | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly
Project Cost Summary |  |  | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost | Estimated Cost
I Specialized Equipment | USD |  | 132296450.242 | 130536639.8219 | 128336322.9219 | 126637114.299 | 115037057.1258 | 113263684.9063 | 324534675.1119 | 329234458.0985 | 297420853.9432 | 294316820.9842 | 293776714.6587 | 290412403.5115 | 212047429.4703 | 210273748.5508 | 238455681.121 | 236695618.7009 | 186744721.7193 | 183713071.557 | 143123840.8003 | 140515987.4187
II Other Equipment | USD |  | 7865263.4613 | 7170273.3 | 8164695.0025 | 7449537.3865 | 13812727.4617 | 5679947.4712 | 10337334.7628 | 11384919.2246 | 9849616.1214 | 8917720.7106 | 10786158.8847 | 10239611.684 | 26446049.8406 | 18490216.373 | 24387474.204 | 23849733.9307 | 4729133.4757 | 3951880.4879 | 3722810.6008 | 3040401.9068
III Civil | USD |  | 21714795.8166 | 19863542.0929 | 22078781.5796 | 20204701.8443 | 18315485.5648 | 14117100.037 | 33185121.9228 | 35630554.2268 | 25873035.4635 | 24130554.9422 | 30696312.5341 | 28226093.0647 | 37585620.4468 | 32970252.2881 | 45357509.9616 | 43499876.5757 | 19714030.611 | 17421232.993 | 17196812.0893 | 15259952.8381
IV Mechanical | USD |  | 21283729.1316 | 19552066.0659 | 21711402.8715 | 19979394.9632 | 15403158.5583 | 11480960.2001 | 33254299.8202 | 35771723.847 | 22809356.4964 | 21206630.6427 | 27402312.6133 | 24971603.9243 | 45509562.4742 | 40817779.1688 | 63834551.0021 | 61641232.9152 | 35042332.6801 | 33293724.3686 | 29195940.2702 | 27637890.9778
V Electrical Assembly & Wiring | USD |  | 9431816.3686 | 8998593.5852 | 9518269.4041 | 9079220.2696 | 6188561.8744 | 5243275.0216 | 20242173.3725 | 22420283.0315 | 11844899.9628 | 10835291.1011 | 21190555.4338 | 20544918.5469 | 13291528.0549 | 12030592.3712 | 21497545.3678 | 20960638.4762 | 14262805.9326 | 13623152.4672 | 10429719.5287 | 9935890.3786
VI Buildings & Structures | USD |  | 3678318.1028 | 3678318.1028 | 3699449.8184 | 3699449.8184 | 3711241.0777 | 3413565.3 | 3762574.7127 | 3762574.7127 | 3503552.3816 | 3503552.3816 | 3720587.6499 | 3720587.6499 | 4070996.1061 | 3815128.0746 | 6916250.6603 | 6916250.6603 | 3336693.1305 | 3336693.1305 | 15625332.0045 | 15625332.0045
VII Engineering & Plant Startup | USD |  | 13722054.3526 | 13587683.8021 | 14081833.2046 | 13943867.2041 | 11759837.9425 | 11644469.6921 | 14527923.8573 | 14671892.3078 | 11835957.9929 | 11720072.0925 | 14217731.8553 | 14078261.1048 | 37377280.8543 | 37028164.8533 | 41779267.7809 | 41479176.8307 | 10639666.2372 | 10534065.9368 | 9922759.8839 | 9824713.0836
Gasification Plant | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Desalination Plant | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 Capture Plant | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal - Contractor's Internal Cost | USD |  | 209992427.4755 | 203387116.7709 | 207590754.8026 | 200993285.7851 | 184228069.6052 | 164843002.6283 | 439844103.5601 | 452876405.4489 | 383137272.3618 | 374630642.8548 | 401790373.6298 | 392193479.486 | 376328467.2472 | 355425881.6799 | 442228280.0977 | 435042528.0897 | 274469383.7865 | 265873820.941 | 229217215.1777 | 221840168.6082
VIII Contractor's Soft & Miscellaneous Costs | USD |  | 97055870.6152 | 92699497.0463 | 96768866.9723 | 92396494.6466 | 81974137.1746 | 70611972.9908 | 190394434.7113 | 198317724.1851 | 157042620.6854 | 151951991.4503 | 171201741.3517 | 165142665.1312 | 176508557.4932 | 163784111.3489 | 217966323.6009 | 213122414.4301 | 126763287.9742 | 121232896.8468 | 102870675.4617 | 98188901.825
Contractor's Price | USD |  | 307048298.0907 | 296086613.8173 | 304359621.7749 | 293389780.4316 | 266202206.7798 | 235454975.6191 | 630238538.2714 | 651194129.634 | 540179893.0472 | 526582634.3052 | 572992114.9814 | 557336144.6172 | 552837024.7405 | 519209993.0288 | 660194603.6986 | 648164942.5198 | 401232671.7607 | 387106717.7878 | 332087890.6394 | 320029070.4332
IX Owner's Soft & Miscellaneous Costs | USD |  | 82903040.4845 | 79943385.7307 | 82177097.8792 | 79215240.7165 | 71874595.8305 | 63572843.4171 | 170164405.3333 | 175822415.0012 | 145848571.1227 | 142177311.2624 | 154707871.045 | 150480759.0466 | 149265996.6799 | 140186698.1178 | 178252542.9986 | 175004534.4803 | 108332821.3754 | 104518813.8027 | 89663730.4726 | 86407849.017
Battery Storage System | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total - Owner's Cost | USD |  | 389951338.5752 | 376029999.5479 | 386536719.6541 | 372605021.1482 | 338076802.6104 | 299027819.0362 | 800402943.6047 | 827016544.6352 | 686028464.17 | 668759945.5676 | 727699986.0264 | 707816903.6638 | 702103021.4204 | 659396691.1466 | 838447146.6972 | 823169477.0001 | 509565493.1361 | 491625531.5905 | 421751621.112 | 406436919.4502
Net Plant Output | MW |  | 341.1887 | 341.1887 | 347.773 | 347.773 | 258.2408 | 258.3028 | 380.2258 | 380.2258 | 264.0813 | 264.0863 | 356.2173 | 356.2223 | 389.5131 | 389.5811 | 489.2671 | 489.2721 | 245.7632 | 245.7632 | 217.408 | 217.408
Price per kW - Contractor's | USD per kW |  | 899.937 | 867.8091 | 875.1674 | 843.6243 | 1030.8295 | 911.5464 | 1657.5374 | 1712.651 | 2045.506 | 1993.9793 | 1608.5465 | 1564.5739 | 1419.3028 | 1332.7392 | 1349.3542 | 1324.7535 | 1632.5986 | 1575.1207 | 1527.4871 | 1472.0207
Cost per kW - Owner's | USD per kW |  | 1142.92 | 1102.1175 | 1111.4626 | 1071.4028 | 1309.1534 | 1157.6639 | 2105.0725 | 2175.0667 | 2597.7927 | 2532.3538 | 2042.8541 | 1987.0089 | 1802.5146 | 1692.5788 | 1713.6798 | 1682.437 | 2073.4002 | 2000.4032 | 1939.9086 | 1869.4663
Contractor's soft cost override, USD/kW | USD/kW | Thermoflow values applied are inconsistent across the page for similarly sized and risky projects. Considered not suitable for comparison across technologies. Applied: USD250/kW for SCGT and recips and USD350/kW for CCGT (additional complexity and risk) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 350 | 350 | 350 | 350 | 250 | 250 | 250 | 250
- value applied | USD |  | 85297250 | 85297250 | 86943250 | 86943250 | 64560250 | 64575750 | 95056500 | 95056500 | 66020250 | 66021500 | 89054250 | 89055500 | 136329550 | 136353350 | 171243450 | 171245200 | 61440750 | 61440750 | 54352000 | 54352000
EPC cost (Contractor's price). Excludes owners costs and connections etc, overnight |  | USD | 295289677.4755 | 288684366.7709 | 294534004.8026 | 287936535.7851 | 248788319.6052 | 229418752.6283 | 534900603.5601 | 547932905.4489 | 449157522.3618 | 440652142.8548 | 490844623.6298 | 481248979.486 | 512658017.2472 | 491779231.6799 | 613471730.0977 | 606287728.0897 | 335910133.7865 | 327314570.941 | 283569215.1777 | 276192168.6082
Owner's cost |  | USD | 35434761.2971 | 34642124.0125 | 35344080.5763 | 34552384.2942 | 29854598.3526 | 27530250.3154 | 64188072.4272 | 65751948.6539 | 53898902.6834 | 52878257.1426 | 58901354.8356 | 57749877.5383 | 61518962.0697 | 59013507.8016 | 73616607.6117 | 72754527.3708 | 40309216.0544 | 39277748.5129 | 34028305.8213 | 33143060.233
Total powerplant |  | USD | 330724438.7726 | 323326490.7834 | 329878085.3789 | 322488920.0793 | 278642917.9579 | 256949002.9437 | 599088675.9873 | 613684854.1028 | 503056425.0452 | 493530399.9974 | 549745978.4653 | 538998857.0244 | 574176979.3169 | 550792739.4815 | 687088337.7094 | 679042255.4604 | 376219349.8409 | 366592319.454 | 317597520.999 | 309335228.8412
Hours |  |  | 289323.0732 | 265910.8731 | 293214.7627 | 269613.6635 | 223981.7689 | 170040.472 | 492918.2009 | 531601.9286 | 343577.8047 | 319027.4032 | 419198.9633 | 388004.3622 | 547203.0681 | 484381.4818 | 744803.2033 | 717932.9988 | 391111.9396 | 361874.3226 | 308344.9493 | 283929.9268
|  | Indicative % of installation cost that is labour | 29.83% | 29.15% | 29.7% | 29.01% | 29.12% | 26.67% | 33.81% | 34.1% | 32.61% | 32.17% | 31.04% | 30.52% | 28.58% | 27.53% | 29.89% | 29.62% | 33.93% | 33.31% | 26.95% | 26.11%
Effective Labor Rates: | Cost per Hour
Civil Account |  |  | 65.0287 | 65.0317 | 65.0265 | 65.0292 | 65.0314 | 65.0364 | 65.0251 | 65.0233 | 65.0263 | 65.0283 | 65.0333 | 65.0365 | 65.0211 | 65.022 | 65.0166 | 65.0173 | 65.0332 | 65.0377 | 65.0322 | 65.0364
Mechanical Account |  |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Electrical Account |  |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
Site ambient conditions: 1.001 bar, 41 C, 20% Rel. Hum. (22.62 C WB), line frequency 50 Hz. Performance on nat gas uno
TECHNICAL: |  |  | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | SCGT | CCGT | CCGT | CCGT | CCGT | RECIP | RECIP | RECIP | RECIP
|  |  | GT13E2 | GT13E2 | SGT5-2000E | SGT5-2000E | 1x9FA | 1x9FA | LM2500 | LM2500 | LM6000 | LM6000 | LMS100 | LMS100 | 9FA | 9FA | GT13E2 | GT13E2 | Jenbacher | Jenbacher | Wartsila | Wartsila
|  |  | DF | GasOnly | DF | GasOnly | DF | GasOnly | GasOnly | DF | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly | DF | GasOnly
Config |  |  | 2 GE GT13E2 | 2 GE GT13E2 | 2 SGT5-2000E | 2 SGT5-2000E | One GE 9FA.04 | One GE 9FA.04 | 12 GE LM2500-G4 | 12 GE LM2500-G4 | 6 GE LM6KPFSPT | 6 GE LM6KPFSPT | 4 GE LMS100PB | 4 GE LMS100PB | One GE 9FA.04 | One GE 9FA.04 | 2 GE GT13E2 | 2 GE GT13E2 | 24 INNIO J920 | 24 INNIO J920 | 12 WRT 18V50SG | 12 WRT 18V50SG
Tflow model |  |  | 509 | 509 | 745 | 745 | 785 | 785 | 833 | 833 | 799 | 799 | 439 | 439 | 785 | 785 | 509 | 509 | 640 | 640 | 468 | 468
Gross kW |  |  | 346217 | 346217 | 352954 | 352954 | 261961 | 261961 | 386282 | 386282 | 268351 | 268351 | 367370 | 367370 | 399231 | 399231 | 500635 | 500635 | 249290 | 249290 | 220528 | 220528
Net kW |  |  | 341189 | 341189 | 347773 | 347773 | 258241 | 258303 | 380226 | 380226 | 264081 | 264086 | 356217 | 356222 | 389513 | 389581 | 489267 | 489272 | 245763 | 245763 | 217408 | 217408
Net HR LHV MJ/MWh |  |  | 9771 | 9771 | 10057 | 10057 | 9610 | 9608 | 9392 | 9392 | 8980 | 8980 | 8720 | 8720 | 6319 | 6318 | 6818 | 6818 | 7836 | 7836 | 7868 | 7868
Gas pressure at skid, Bara |  |  | 26.6 | 26.6 | 20.75 | 20.75 | 28.37 | 28.37 | 37.61 | 37.61 | 50.91 | 50.91 | 60.21 | 60.21 | 28.37 | 28.37 | 26.6 | 26.6 | 11.35 | 11.35 | 6.993 | 6.993
Water (kg/s):
- Fogger |  |  | 6.575 | 6.575 | 6.565 | 6.565 | 3.899 | 3.899 | 6.601 | 6.601 | 4.687 | 4.687 | 5.249 | 5.249 | 3.899 | 3.899 | 6.575 | 6.575 | 0 | 0 | 0 | 0
- GT injection or ext cooling |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.038 | 8.038 | 0 | 0
- Steam cycle (note zero blowdown in model) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0285 | 0.0285 | 0.0149 | 0.0149 | 0 | 0 | 0 | 0
- Cooling tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.4 | 127.4 | 174.3 | 174.3 | 0 | 0 | 0 | 0
Site (incl switchyard):
- Area, Ha |  |  | 2.69 | 2.278 | 2.604 | 2.201 | 2.446 | 1.815 | 3.849 | 4.568 | 3.233 | 2.751 | 5.7 | 4.826 | 3.96 | 3.084 | 4.11 | 3.643 | 3.068 | 2.45 | 2.517 | 2.05
- Lx m |  |  | 188 | 159 | 188 | 159 | 183 | 151 | 157 | 187 | 179 | 152 | 185 | 157 | 265 | 234 | 253 | 224 | 149 | 119 | 157 | 128
- Ly m |  |  | 143 | 143 | 138 | 138 | 133 | 120 | 244 | 244 | 181 | 181 | 308 | 308 | 149 | 132 | 163 | 163 | 206 | 206 | 160 | 160

## Rawlinsons
Factors extracted from Rawlinson's Australian Cost Handbook, 2026 ed
Factors extracted to evaluate locational cost relativities between 'near Melbourne' - the reference location for IASR/GenCost, and 'near Perth'
Costs are Q2 2026 uno
Regional indices (re Perth = 100)
Location | Index | Approx Distance from Perth CBD (km) |  |  |  | Site | Selected location | Regional factor adopted | These are costs at regional location re Perth = 100
Perth | 100 | 0 |  |  |  | Three Springs | Moora | 125
Perth CBD | 103 | 0 |  |  |  | Eneabba | Jurien Bay | 120
Yanchep | 105 | 55 |  |  |  | Badgingarra | Jurien Bay | 120
Mandurah | 100 | 75 |  |  |  | Cataby | Jurien Bay | 120
Pinjarra | 110 | 85 |  |  |  | Gingin | Yanchep | 105
Toodyay | 115 | 85 |  |  |  | Muchea | Yanchep | 105
Northam | 110 | 100 |  |  |  | Pinjar | Yanchep | 105
York | 110 | 100 |  |  |  | Neerabup | Yanchep | 105
Harvey | 110 | 140 |  |  |  | Average |  | 113.125
Bunbury | 105 | 175
Moora | 125 | 180
Wongan Hills | 125 | 185 |  |  |  | Perth factor - labour | 1.0545 |  | Costs at Perth re Mebourne environs = 100
Narrogin | 120 | 190 |  |  |  | Perth factor - other | 1 |  | Costs at Perth re Mebourne environs = 100
Collie | 115 | 210
Jurien Bay | 120 | 220
Dalwallinu | 125 | 250
Merredin | 120 | 260
Bridgetown | 115 | 270
Margaret River | 125 | 275
Katanning | 125 | 280
Manjimup | 120 | 310
Factories (buildings), large span, heavy industries, tilt-up
|  | Melbourne | Perth | Factor
Range min | $/m2 | 1535 | 1780
Range max | $/m2 | 1655 | 1915
Mid (calc.) | $/m2 | 1595 | 1847.5 | 1.1583
Raft foundations, 25MPa incl reinforement
|  | Melbourne | Perth | Factor
Value | $/m3 | 1260 | 1290 | 1.0238
Structural steelwork (250 UC 89.5, plain steel, supply and erect)
|  | Melbourne | Perth | Factor
Value | $/m2 | 920 | 890 | 0.96739
Labour (Average contract charge out rates)
$/h
| Melbourne |  |  |  | Perth
Trade | Range Min | Range Max | Mid(calc.) |  | Range Min | Range Max | Mid(calc.) |  | Factor
Bricklayer | 116 | 125 | 120.5 |  | 116 | 120 | 118 |  | 0.97925
Carpenter/Joiner | 116 | 125 | 120.5 |  | 117 | 122 | 119.5 |  | 0.9917
Painter/Glazier | 114.5 | 124 | 119.25 |  | 107 | 110 | 108.5 |  | 0.90985
Plasterer | 116 | 125 | 120.5 |  | 111 | 115 | 113 |  | 0.93776
Plumber/Drainer | 124 | 130 | 127 |  | 132.5 | 136.5 | 134.5 |  | 1.0591
Labourer Group 1 | 116 | 125 | 120.5 |  | 109 | 113 | 111 |  | 0.92116
Labourer Group 2 | 114.5 | 124 | 119.25 |  | 107 | 111 | 109 |  | 0.91405
Labourer Group 3 | 113 | 121.5 | 117.25 |  | 107 | 111 | 109 |  | 0.92964
Labourer Group 4 | 111 | 118.5 | 114.75 |  | 102.5 | 110 | 106.25 |  | 0.92593
Refrigeration Fitter | 117.5 | 125.5 | 121.5 |  | 129.5 | 133.5 | 131.5 |  | 1.0823
Sheet Metalworker Class 1 | 114.5 | 124.5 | 119.5 |  | 124.5 | 131.5 | 128 |  | 1.0711
Sheet Metalworker Class 2 | 109 | 114 | 111.5 |  | 124.5 | 131.5 | 128 |  | 1.148
Lagger | 117.5 | 125.5 | 121.5 |  | 123 | 130.5 | 126.75 |  | 1.0432
Electrician | 119 | 125.5 | 122.25 |  | 128.5 | 132.5 | 130.5 |  | 1.0675
Plumber | 125.5 | 131.5 | 128.5 |  | 131.5 | 137.5 | 134.5 |  | 1.0467
Electrical Installer | 125.5 | 131.5 | 128.5 |  | 129.5 | 141.5 | 135.5 |  | 1.0545

## Land cost
Landgate for ERA
2025-11-28
| Location | Land Area (Hectares) | Rate per Hectare | Assessed Value (Rounded)
| Three Springs | 7.3 | 20000 | 145000
| Eneabba | 7.3 | 40000 | 290000
| Badgingarra | 7.3 | 40000 | 290000
| Cataby | 7.3 | 40000 | 290000
| Gingin | 7.3 | 100000 | 730000
| Muchea | 7.3 | 1300000 | 9490000
| Pinjar | 7.3 | 1250000 | 9125000
| Neerabup | 7.3 | 1500000 | 10950000
| Average | 7.3 | 536250 | 3913750